62-761.500 Performance Standards for Category C Storage Tank Systems.

(1) General performance standards. UST Category-C systems shall be constructed and installed in accordance with the requirements of this section. UST Category-C systems shall be made of, or internally lined with, materials that are compatible with the regulated substance stored in the system. The following requirements are applicable to UST systems:

(a) Siting. Persons are advised that, pursuant to paragraphs 62-521.400(1)(l)-(n) and subsection (2), F.A.C., no storage tank shall be installed within 500 feet of any existing community water supply system or any existing non-transient non-community water supply system. No Category-C system shall be installed within 100 feet of any other existing potable water supply well. These prohibitions shall not apply to the replacement of an existing storage tank system within the same excavation or the addition of new storage systems meeting the standards for Category-C systems at an existing facility.

(b) Spill containment. USTs shall be installed with a spill containment system at each tank fill connection. The spill containment system shall be a fixed component that is designed to prevent a discharge of regulated substances when the transfer hose or pipe is detached from the tank fill pipe. The spill containment system shall meet the requirements of paragraph 62-761.500(1)(d), F.A.C.

(c) Dispensing systems.

1. The dispensing system used for transferring fuels from storage tanks shall be installed and maintained in accordance with the provisions of NFPA 30 and Chapters 2, 4 and 9 of NFPA 30A.

2. Dispensers shall be designed, constructed, and maintained to provide access for examination and removal of collected product and accumulated water from dispenser liners.

(d) Secondary containment.

1. The materials used for secondary containment shall be:

a. Impervious to the regulated substance and able to withstand deterioration from external environmental conditions;

b. Non-corrosive or of corrosion-protected materials;

c. Capable of containing regulated substances for at least 30 days; and

d. Of sufficient thickness and strength to withstand hydrostatic forces at maximum capacity to prevent a discharge during its operating life.

2. Liners, unless previously approved by the Department, shall be approved by the Department in accordance with subsection 62-761.850(2), F.A.C. Liners shall not be constructed or consist of naturally occurring in-situ soils.

3. Secondary contaiment constructed of concrete shall be:

a. Designed and constructed in accordance with ACI 350R-89 and ACI 224R-89; or

b. Designed, evaluated, and certified by a professional engineer registered in the State of Florida that the concrete secondary containment system meets the General Construction Requirements specified in subparagraph 62-761.500(1)(d)1., F.A.C.

4. For cathodically protected tanks and integral piping, secondary containment systems shall not interfere with the operation of the cathodic protection system.

5. Storage tank system equipment with closed interstitial spaces, such as double-walled USTs and double-walled integral piping in contact with the soil that is connected to USTs, shall be designed, constructed and installed to allow for the detection of a breach of integrity in the inner or outer wall by the monitoring of the interstitial space in accordance with paragraph 62-761.640(3)(a), F.A.C. A breach of integrity test shall be performed before the storage tank system is put into service.

6. Secondary containment systems shall be designed and installed to direct any release to a monitoring point or points.

7. Airport and seaport hydrant pits. Underground hydrant pits shall be installed with a spill catchment basin, secondary containment, or other spill prevention equipment to prevent the discharge of pollutants during fueling of aircraft, vessels, or at any other time the hydrant system is in use. Any such equipment shall be sealed to and around the hydrant piping with an impervious, compatible material.

8. Field-fabricated dispenser liners and piping sumps installed before July 13, 1998 do not have to be approved in accordance with Rule 62-761.850, F.A.C.

(e) Cathodic protection.

1. Test stations. Cathodic protection systems shall be designed, constructed, and installed with at least one test station or method of monitoring to allow for a determination of current operating status. Cathodic protection test stations shall provide direct access to the soil electrolyte in close proximity to each cathodically protected structure for placement of reference electrodes, and monitoring wires that connect directly to cathodically protected structures. Facilities where direct access to soil in close proximity to cathodically protected structures is present, and where electrical connections to cathodically protected structures can be conveniently accomplished, need not have separate dedicated cathodic protection test stations.

2. The cathodic protection system shall be operated and maintained in accordance with paragraph 62-761.700(1)(b), F.A.C.

3. Any field-installed cathodic protection system shall be designed by a Corrosion Professional.

(f) Relocation of USTs. Tanks that have been removed and that are to be reinstalled at a different location shall:

1. Be recertified that all original warranties are confirmed by the original manufacturer or the manufacturer’s successor, and be reinstalled in accordance with the standards in Rule 62-761.500, F.A.C., that were in effect on July 13, 1998; or

2. Be recertified by a professional engineer registered in the State of Florida that the UST meets all applicable standards of Rule 62-761.500, F.A.C., in effect on July 13, 1998; and

3. Proof of recertification shall be provided to the Department and County prior to the completion of installation. The provisions of subsection 62-761.850(2), F.A.C., do not apply to the requirements of this subparagraph.

(g) Reuse of storage tanks. Unless it is recertified for use by a professional engineer registered in the State of Florida, or is recertified by the manufacturer, and is brought into service in accordance with Rule 62-761.500, F.A.C.:

1. A UST can not be used or reused as an AST for the storage of regulated substances; and

2. An AST can not be used or reused as a UST for the storage of regulated substances.

(2) Installation.

(a) All components of a storage tank system shall be installed in accordance with the manufacturer’s instructions.

(b) All storage tank systems shall be installed according to the applicable provisions of NFPA 30 and 30A, PEI/RP100-97, and API RP 1615.

(c) A Certified Contractor shall perform the installation of storage tank systems containing pollutants, including tanks, integral piping (excluding drop tubes), overfill protection and spill containment equipment, internal release detection equipment, cathodic protection systems, secondary containment systems, and dispensing systems, if the installation of the storage tank system component disturbs the backfill, or where the integral piping is connected or disconnected during installation.

(d) A tightness test shall be performed on the tank and integral piping before any storage tank system is placed into service unless the system’s equipment approval specifies otherwise.

(3) Tank construction standards.

(a) Fiberglass reinforced plastic tanks shall be constructed in accordance with UL 1316 and ASTM Standard D4021-86, or certified by a nationally recognized laboratory that these standards are met.

(b) Cathodically protected steel tanks shall be:

1. Constructed in accordance with UL 58 and UL 1746, or as applicable;

2. Constructed in accordance with STI #STI-P3® Specification and Manual for External Corrosion Protection of Underground Steel Storage Tanks; or

3. Certified by a Nationally Recognized Laboratory that these standards are met, and constructed and designed by a corrosion professional in accordance with NACE International Standard RP0285-95 for any field-installed cathodic protection system.

(c) Steel tanks coated with a fiberglass reinforced plastic composite shall be constructed in accordance with UL-58 and either UL 1746, STI ACT 100® (F894), or certified by a nationally recognized laboratory that one of these standards is met.

(d) Storage tanks constructed of any other material, design, or corrosion protection shall be approved by the Department in accordance with subsection 62-761.850(2), F.A.C.

(e) Any new tank manufactured with previously used or remanufactured components shall be certified before being installed as meeting the applicable standards by Underwriters Laboratory, by a comparable certified product testing laboratory, or by a professional engineer registered in the State of Florida.

(f) Tanks shall be constructed or installed to provide for interstitial monitoring.

(4) Secondary containment. All tanks installed or constructed at a facility after July 13, 1998 shall have secondary containment.

(5) Overfill protection.

(a) At a minimum, fillbox covers shall be marked in accordance with API RP 1637, or with an equivalent method approved by the Department in accordance with subsection 62-761.850(2), F.A.C.

(b) USTs shall be equipped with a system that either:

1. Automatically shuts off flow to the tank when the tank is no more than 95% full;

2. Restricts flow to the tank when the tank is no more than 90% full;

3. Alerts the transfer operator when the tank is no more than 90% full by triggering a high level alarm;

4. Alerts the transfer operator with a high level alarm set at 400 gallons below tank top, but no less than one minute before overfilling; or

5. Automatically shuts off flow into the tank so that none of the fittings located on top of the tank are exposed to product due to overfilling.

(6) Dispenser liners.

(a) Storage tank systems installed or replaced after July 13, 1998, shall be installed with liners meeting the performance standards of paragraph 62-761.500(1)(d), F.A.C., beneath the union of the piping and the dispenser.

(b) Hydrostatic tests shall be performed for all dispenser liners before placing the system into service. The duration of the tests shall be at least:

1. Twenty-four hours for field-fabricated dispenser liners; or

2. Three hours for factory-made dispenser liners.

(c) Dispenser liners shall be installed to allow for interstitial monitoring in accordance with paragraph 62-761.640(3)(a), F.A.C.

(7) Piping sumps.

(a) Piping sumps installed after July 13, 1998, shall meet the performance standards of paragraph 62-761.500(1)(d), F.A.C. The sumps shall be designed, constructed, and installed to minimize water entering the sump.

(b) Hydrostatic tests shall be performed for all piping sumps before placing the system into service. The duration of the tests shall be at least:

1. Twenty-four hours for field-fabricated piping sumps; or

2. Three hours for factory-made piping sumps.

(c) Piping sumps shall be installed to allow for interstitial monitoring in accordance with paragraph 62-761.640(3)(a), F.A.C.

(8) Integral piping for underground storage tank systems.

(a) Installation.

1. All integral piping shall be installed in accordance with the manufacturer’s instructions, if applicable.

2. All integral piping shall be installed according to the applicable provisions of NFPA 30, NFPA 30A, and ASME B31.4.

3. A pressure test shall be performed for underground bulk product piping before the piping system is placed into service. Tightness tests for underground small diameter piping connected to USTs are subject to paragraph 62-761.500(2)(d), F.A.C.

4. All piping that is not in contact with the soil, installed after July 13, 1998, shall meet the construction standards in paragraphs 62-761.500(8)(a)-(d), F.A.C.

(b) Integral piping construction standards.

1. Fiberglass reinforced plastic piping or other non-metallic piping installed at a facility shall be listed with UL 971, UL 567, certified by a Nationally Recognized Laboratory that these standards are met, or approved in accordance with subparagraph 62-761.500(8)(b)3., F.A.C.

2. Coated steel piping shall be constructed in accordance with ASME B31.4. Integral piping in contact with the soil shall be cathodically protected in accordance with API RP 1632, NACE International RP-0169-96, and STI R892-96.

3. Integral piping constructed of other materials, design, or corrosion protection shall be approved by the Department in accordance with subsection 62-761.850(2), F.A.C.

(c) Small diameter piping.

1. Pressurized small diameter piping systems connected to dispensers shall be installed with shear valves or emergency shutoff valves in accordance with NFPA 30A, Section 4-3.6, if applicable. These valves shall be designed to close automatically if a dispenser is dislodged from the integral piping. The valves shall be rigidly anchored independently of the dispenser. For underground small diameter piping, the valves shall be checked at the time of installation by a certified contractor to confirm that the automatic closing function of the valve operates properly and that the valve is properly anchored.

2. Gravity-fed small diameter integral piping systems must be installed with an isolation valve at the point of connection to the storage tank to prevent the discharge of regulated substances in the case of piping failure. The valve shall meet the standards of NFPA 30A, Section 2-1.7.

3. Swing-joints shall not be installed.

(d) Bulk product piping. Bulk product piping shall be constructed and installed in accordance with NFPA 30, and ASME B31.4.

(e) Secondary containment.

1. Small diameter integral piping that is in contact with the soil or that transports regulated substances over surface waters of the state shall have secondary containment.

2. Bulk product piping that is in contact with the soil shall have secondary containment.

3. Remote fill piping that is in contact with the soil shall have secondary containment.

4. The following integral piping systems are exempt from the requirements for secondary containment:

a. Integral piping that is in contact with the soil, and that is connected to storage tanks containing high viscosity regulated substances; and

b. Vertical fill pipes equipped with a drop tube.

Specific Authority 376.303 FS. Law Implemented 376.303 FS. History–New 12-10-90, Amended 5-4-92, Formerly 17-761.500, Amended 9-30-96, 7-13-98, 6-21-04.