62-699.310 Classification and Staffing of Domestic Wastewater or Water Treatment Plants and Water Distribution Systems.

This section applies to all domestic wastewater treatment plant permittees or suppliers of water except suppliers of water who own or operate a transient non-community water system serving only businesses other than public food service establishments and using only ground water as a source of supply. Licensed operators are not required for transient non-community water systems serving only businesses other than public food service establishments and using only ground water as a source of supply.

(1) Domestic wastewater treatment plant permittees and suppliers of water shall employ only persons appropriately licensed under Chapter 62-602, F.A.C., to be in on-site charge of the operation, supervision, or maintenance of a domestic wastewater or water treatment plant during any part of any day. Beginning May 1, 2011, suppliers of water shall employ only persons appropriately licensed under Chapter 62-602, F.A.C., to be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 under the tables in subparagraphs 62-699.310(2)(f)1. and 2., F.A.C.

(2) Permittees and suppliers of water shall employ licensed operators on-site at their domestic wastewater or water treatment plant(s) to fulfill the time and visit requirements specified in paragraphs (a) through (e) below. Beginning May 1, 2011, suppliers of water shall employ licensed operators to staff their water distribution system as specified in paragraph (f) below.

(a) Classification and Staffing Requirements for Domestic Wastewater Treatment Plants Other than Those Discussed Separately in paragraphs (b) through (d) below. All flow values used in this paragraph refer to the permitted capacity of the domestic wastewater treatment plant.

| 1. Domestic Wastewater Treatment Plant Category I |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Processes to meet permit limits for total nitrogen with or without filtration; processes to meet permit limits for total phosphorus with or without filtration; or membrane processes, including microfiltration, ultrafiltration, nanofiltration, reverse osmosis, and membrane bioreactors. | - 3.0 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 0.5 MGD up to 3.0 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 0.1 MGD up to 0.5 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.05 MGD up to 0.1 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ Less than 0.05 MGD Staffing by Class C or higher operator: 1 hour/day for 5 days/week and one visit each weekend. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | - Not Applicable |

| 2. Domestic Wastewater Treatment Plant Category II |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Activated sludge processes, except extended aeration, with or without filtration. | - 5.0 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 1.0 MGD up to 5.0 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 0.25 MGD up to 1.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.1 MGD up to 0.25 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ Less than 0.1 MGD Staffing by Class C or higher operator: 1/2 hour/day for 5 days/week and one visit each weekend. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | - Not Applicable |

| 3. Domestic Wastewater Treatment Plant Category III |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Extended aeration, including oxidation ditches, with or without filtration. | - 8.0 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 2.0 MGD up to 8.0 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 0.5 MGD up to 2.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.25 MGD up to 0.5 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit each weekend. ________________ 25,000 GPD up to 0.25 MGD Staffing by Class C or higher operator: 1/2 hour/day for 5 days/week and one visit each weekend. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | 10,000 GPD up to 25,000 GPD Staffing by Class D or higher operator: 3 visits/week on nonconsecutive days for a total of 1 1/2 hours/week. ________________ 2,000 up to 10,000 GPD Staffing by Class D or higher operator: 2 visits/week on nonconsecutive days for a total of 1 hour/week. There shall be no more than 5 days between the last visit in one week and the first visit in the next week. ________________ For all of the above plants, the lead/chief operator must be Class D or higher. |

| 4. Domestic Wastewater Treatment Plant Category IV |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Either of the following processes with or without filtration: trickling filters or rotating biological contactors. | - 10 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 3.0 MGD up to 10 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 2.0 MGD up to 3.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.75 MGD up to 2.0 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ 25,000 GPD up to 0.75 MGD Staffing by Class C or higher operator: 1/2 hour/day for 5 days/week and one visit each weekend. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | 2,000 up to 25,000 GPD Staffing by Class D or higher operator: 2 visits/week on nonconsecutive days for a total of 1 hour/week. There shall be no more than 5 days between the last visit in one week and the first visit in the next week. The lead/chief operator must be Class D or higher. |

(b) Staffing Requirements for Domestic Wastewater Treatment Plants that Provide Reclaimed Water to a Reuse System Permitted Under Part III of Chapter 62-610, F.A.C.

1. The plant category shall be established in accordance with paragraph (a) above.

2. Additional minimum staffing requirements are provided in subsections 62-610.462(2) and (3), F.A.C., which shall be used in conjunction with the requirements in paragraph (a) above, with the most stringent requirements governing. Reductions in staffing requirements below the minimum established in subsections 62-610.462(2) and (3), F.A.C., shall not be allowed.

(c) Staffing Requirements for Domestic Wastewater Treatment Plants that Provide Reclaimed Water to a Reuse System Permitted Under Part V of Chapter 62-610, F.A.C.

1. The plant category shall be established in accordance with paragraph (a) above.

2. Additional minimum staffing requirements are provided in subsections 62-610.567(3), (4), and (5), F.A.C., which shall be used in conjunction with the requirements in paragraph (a) above, with the most stringent requirements governing. Reductions in staffing requirements below the minimum established in subsections 62-610.567(3), (4), and (5), F.A.C., shall not be allowed.

(d) Staffing Requirements for Residuals Management Facilities. Staffing requirements are provided in paragraph 62-640.880(2)(i), F.A.C.

(e) Classification and Staffing Requirements for Water Treatment Plants. All flow values used in this paragraph refer to the permitted maximum-day operating capacity of the water treatment plant.

| 1. Water Treatment Plant Category I |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Conventional filtration (coagulation, flocculation, sedimentation, and filtration); direct filtration, (coagulation and filtration); or lime softening. | - 5.0 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 1.0 MGD up to 5.0 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 0.3 MGD up to 1.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.1 MGD up to 0.3 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ Less than 0.1 MGD Staffing by Class C or higher operator: 2 hours/day for 5 days/week and one visit on each weekend day. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | Not Applicable |

| 2. Water Treatment Plant Category II |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Membrane processes, including electrodialysis, electrodialysis reversal, microfiltration, ultrafiltration, nanofiltration, and reverse osmosis. | - 6.5 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 1.0 MGD up to 6.5 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 0.5 MGD up to 1.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.1 MGD up to 0.5 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ Less than 0.1 MGD Staffing by Class C or higher operator: 1 hour/day for 5 days/week and one visit on each weekend day. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | Not Applicable |

| 3. Water Treatment Plant Category III |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Activated carbon processes; diatomaceous earth filtration; iron exchange for removal of any primary contaminant; iron and manganese removal (oxidation, detention, and filtration); or slow sand filtration. | - 8.0 MGD and above Staffing by Class C or higher operator: 24 hours/day for 7 days/week. The lead/chief operator must be Class A. | - 2.0 MGD up to 8.0 MGD Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 1.0 MGD up to 2.0 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.5 MGD up to 1.0 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ 0.25 MGD up to 0.5 MGD Staffing by Class C or higher operator: 1 hour/day for 5 days/week and one visit on each weekend day. ________________ Less than 0.25 MGD Staffing by Class C or higher operator: 5 visits/week and one visit each weekend for a total of 1.8 hours/week. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | Not Applicable |

| 4. Water Treatment Plant Category IV |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Aeration for removal of any primary contaminant; alkalinity/pH adjustment; chloramination; chlorine dioxide for oxidation or disinfection; fluoridation; ion exchange for removal of any secondary contaminant, sulfide, or any unregulated contaminant; or ozonation. | Not Applicable | - 10 MGD and above Staffing by Class C or higher operator: 16 hours/day for 7 days/week. The lead/chief operator must be Class B or higher. | - 5.0 MGD up to 10 MGD Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 3.0 MGD up to 5.0 MGD Staffing by Class C or higher operator: 3 hours/day for 5 days/week and one visit on each weekend day. ________________ 1.0 MGD up to 3.0 MGD Staffing by Class C or higher operator: 1 hour/day for 5 days/week and one visit on each weekend day. ________________ 0.1 MGD up to 1.0 MGD Staffing by Class C or higher operator: 5 visits/week and one visit each weekend for a total of 1.2 hours/week. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | Less than 0.1 MGD Staffing by a Class D or higher operator: 3 visits/week on nonconsecutive days for a total of 0.6 hour/week. The lead/chief operator must be Class D or higher. |

| 5. Water Treatment Plant Category V |  |  |  |  |
| --- | --- | --- | --- | --- |
| Treatment Process | - Class A | - Class B | - Class C | - Class D |
| Aeration for removal of any secondary contaminant, sulfide, or any unregulated contaminant; chlorination; corrosion control inhibitor addition; hypochlorination; iron or manganese sequestration; or ultraviolet radiation. | Not Applicable | Not Applicable | - 5.0 MGD and above Staffing by Class C or higher operator: 6 hours/day for 5 days/week and one visit on each weekend day. ________________ 3.0 MGD up to 5.0 MGD Staffing by Class C or higher operator: 1 hour/day for 5 days/week and one visit on each weekend day. ________________ 0.25 MGD up to 3.0 MGD Staffing by Class C or higher operator: 5 visits/week and one visit each weekend for a total of 0.6 hour/week. ________________ For all of the above plants, the lead/chief operator must be Class C or higher. | 50,000 GPD up to 0.25 MGD Staffing by Class D or higher operator: 3 visits/week on nonconsecutive days for a total of 0.3 hour/week. ________________ Less than 50,000 GPD Staffing by a Class D or higher operator: 2 visits/week on nonconsecutive days for a total of 0.2 hour/week. There shall be no more than 5 days between the last visit in one week and the first visit in the next week. ________________ For all of the above plants, the lead/chief operator must be Class D or higher. |

(f) Classification and Staffing Requirements for Water Distribution Systems. For the purpose of this paragraph, the number of persons served by a water distribution system is the retail number of persons served by that individual system and excludes persons served by regulated consecutive systems receiving water from that system.

| 1. Water Distribution System Category I |  |  |  |  |
| --- | --- | --- | --- | --- |
| Distribution System | - Level 1 | - Level 2 | - Level 3 | - Level 4 |
| Distribution system connected to a Class A, B, or C water treatment plant. | Serving 100,000 or more persons. Beginning May 1, 2011, the lead/chief operator must be a Level 1 water distribution system operator or a Class C or higher water treatment plant operator. Additionally, beginning May 1, 2011, a Level 3 or higher water distribution system operator or a Class C or higher water treatment plant operator shall be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 below unless the activity is being performed by a licensed underground utility and excavation contractor or licensed plumbing contractor. | Serving at least 10,000 persons and less than 100,000 persons. Beginning May 1, 2011, the lead/chief operator must be a Level 2 or higher water distribution system operator or a Class C or higher water treatment plant operator. Additionally, beginning May 1, 2011, a Level 3 or higher water distribution system operator or a Class C or higher water treatment plant operator shall be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 below unless the activity is being performed by a licensed underground utility and excavation contractor or licensed plumbing contractor. | Serving at least 1,000 persons and less than 10,000 persons. Beginning May 1, 2011, the lead/chief operator must be a Level 3 or higher water distribution system operator or a Class C or higher water treatment plant operator. Additionally, beginning May 1, 2011, a Level 3 or higher water distribution system operator or a Class C or higher water treatment plant operator shall be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 below unless the activity is being performed by a licensed underground utility and excavation contractor or licensed plumbing contractor. | Serving less than 1,000 persons2. Beginning May 1, 2011, the lead/chief operator must be a Level 4 or higher water distribution system operator or a Class D or higher water treatment plant operator. Additionally, beginning May 1, 2011, a Level 4 or higher water distribution system operator or a Class D or higher water treatment plant operator shall be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 below unless the activity is being performed by a licensed underground utility and excavation contractor or licensed plumbing contractor. |
| 1 The following water distribution system operation or maintenance activities may affect water quality or quantity: cleaning (swabbing, pigging, scraping, or air-purging) existing water mains; tapping, depressurizing/dewatering, or disinfecting existing water mains; dewatering, cleaning, or disinfecting existing finished-water storage tanks; and manually operating existing pumps, or adjusting existing automatic pump controls or automatic control valves, as necessary to regulate water distribution system flows or pressures. 2 For wholesale systems, a Category I water distribution system serving less than 1,000 persons shall be classified as a Level 3 water distribution system. |  |  |  |  |

| - 2. Water Distribution System Category II |  |  |  |  |
| --- | --- | --- | --- | --- |
| Distribution System | - Level 1 | - Level 2 | - Level 3 | - Level 4 |
| Distribution system connected to a Class D water treatment plant. | Not Applicable | Not Applicable | Not Applicable | Beginning May 1, 2011, the lead/chief operator must be a Level 4 or higher water distribution system operator or a Class D or higher water treatment plant operator. Additionally, beginning May 1, 2011, a Level 4 or higher water distribution system operator or a Class D or higher water treatment plant operator shall be in on-site charge of any water distribution system operation or maintenance activity that may affect water quality or quantity and that is listed in Footnote 1 below unless the activity is being performed by a licensed underground utility and excavation contractor or licensed plumbing contractor. |
| 1 Water distribution system operation and maintenance activities that may affect water quality or quantity include the following: cleaning (swabbing, pigging, scraping, or air-purging) existing or repaired water mains; tapping, depressurizing/dewatering, or disinfecting existing or repaired water mains; dewatering, cleaning, or disinfecting existing or repaired finished-water storage tanks; and manually operating existing pumps, or adjusting automatic pump controls or automatic control valves, as necessary to regulate water distribution system flows or pressures. |  |  |  |  |

Specific Authority 403.869, 403.88(4) FS. Law Implemented 403.853(6), 403.867, 403.875(1)(f), 403.88(1), (2), (3) FS. History–New 11-17-70, Revised 10-24-74, Amended 12-25-75, 6-10-76, 1-12-81, Formerly 17-16.12 and 17-16.13, Amended 5-8-85, Formerly 17-16.370, 17-602.370, 17-699.310, Amended 10-15-07.