- 25-30.262 Meter Accuracy Requirements.

Each utility shall employ water meters which register within the accuracy limits set forth in this chart:

Accuracy limits in percentages

|  | Maximum | Intermediate | Minimum Rate |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Meter Type | Rate | Rate |  | New | Repaired |  |
| Displacement | 98.5-101.5 | 98.5-101.5 |  | 95-101.5 | 90-101.5 |  |
| Current | 97-102 | None |  | 95-102 | 90-102 |  |
| Compound* | 97-103 | 97-103 |  | 95-103 | 90-103 |  |

*The minimum required accuracy for compound meters at any rate within the “changeover” range of flows shall be 85%.

Rulemaking Authority 350.127(2), 367.121 FS. Law Implemented 367.121(1)(a), 367.122(1) FS. History–New 9-12-74, Formerly 25-10.92, 25-10.092, Amended 11-10-86.