AGENCY FOR HEALTH CARE ADMINISTRATION

Division of Health Quality Assurance

RULE NOS.: RULE TITLES:

59A-26.001 Purpose and Intent

59A-26.002 Definitions

59A-26.003 License Required

59A-26.004 Classification of Deficiencies

59A-26.005 Licensure Procedure, Fees and Exemptions

59A-26.006 Responsibilities for Operation

59A-26.007 Fiscal Standards

59A-26.0075 Fiscal Prohibitions, Kickbacks and Referrals

59A-26.008 Admission Policies and Requirements

59A-26.009 Personnel Standards

59A-26.010 Training, Habilitation, Active Treatment Professional, and Special Programs and Services

59A-26.011 Dietary Services

59A-26.012 Dental Services

59A-26.013 Psychological Services

59A-26.014 Drugs and Pharmaceutical Services

59A-26.015 Administration of Medications to ICF/DD Residents by Unlicensed Medication Assistants

59A-26.016 Requirements for Administration of Medication to Residents by Unlicensed Medication

59A-26.017 Training and Validation Required for Unlicensed Medication Assistants

59A-26.018 Plant Maintenance and Housekeeping

59A-26.019 Fire Protection, Life Safety, Systems Failure and External Emergency Communication

59A-26.020 Plans Submission and Fees Required

59A-26.021 Physical Plant Codes and Standards for ICF/DD

59A-26.022 Construction and Physical Environment Standards

59A-26.023 Disaster Preparedness

PURPOSE AND EFFECT: The Agency proposes to adopt licensing rules and minimum standards of program quality and adequacy of care for Intermediate Care Facilities for the Developmentally Disabled, referred to as ICF/DD in accordance with sections 400.960 and 400.969, F.S. The intent of this rule is to ensure services are provided that meet the specific needs of individual residents, overcome barriers to increase independence and productive living, and result in an improved quality of life. In addition, the rule defines and limits the size and design characteristics of an ICF/DD facility to establish optimum environments in which service delivery occurs. This rule reflects the ability of the State of Florida to specify program requirements and residential requirements including facility and living unit size and design. The Agency intends to adopt 59A-26.001 through 59A-26.023.

SUMMARY: Adopt rules pertaining to Intermediate Care Facilities for the Developmentally Disabled.

SUMMARY OF STATEMENT OF ESTIMATED REGULATORY COSTS: No statement of estimated regulatory cost has been prepared.

Any person who wishes to provide information regarding the statement of estimated regulatory costs or to provide a proposal for a lower cost regulatory alternative must do so in writing within 21 days of this notice.

SPECIFIC AUTHORITY: 400.967 FS.

LAW IMPLEMENTED: 400.967 (2) FS.

IF REQUESTED WITHIN 21 DAYS OF THE DATE OF THIS NOTICE, A HEARING WILL BE HELD AT THE DATE, TIME AND PLACE SHOWN BELOW (IF NOT REQUESTED, THIS HEARING WILL NOT BE HELD):

DATE AND TIME: April 18, 2006, 1:30 p.m.. – 3:30 p.m.

PLACE: Agency for Health Care Administration, 2727 Mahan Drive, Building #3, Conference Room D, Tallahassee, Florida 32308

THE PERSON TO BE CONTACTED REGARDING THE PROPOSED RULES IS:

Kimberly Smoak, Long Term Care Unit, 2727 Mahan Drive, Tallahassee, Florida, or call (850)488-5861

THE FULL TEXT OF THE PROPOSED RULES IS:

MINIMUM STANDARDS FOR INTERMEDIATE CARE FACILITIES FOR THE DEVELOPMENTALLY DISABLED

59A-26.001 Purpose and Intent.

The Agency adopts the following licensing rules and minimum standards of program quality and adequacy of care for Intermediate Care Facilities for the Developmentally Disabled, hereafter referred to as ICF/DD in accordance with Sections 400.962 and 400.967, F.S. The intent of this rule is to ensure services are provided that meet the specific needs of individual residents, overcome barriers to increase independence and productive living, and result in an improved quality of life. In addition, the rule defines and limits the size and design characteristics of an ICF/DD to establish optimum environments in which service delivery occurs. This rule reflects the ability of the State of Florida to specify program requirements and residential requirements including facility and living unit size and design.

Specific Authority 400.967(2), (c) FS. Law Implemented 400.967(2) FS. History–New________

59A-26.002 Definitions.

Definitions as they appear in Chapter 400, Part XI, Florida Statutes and those contained herein must apply.

(1) Active Treatment - As defined in 42 CFR 483.440 (a)(1) and (2), which states, "Active treatments refers to aggressive, consistent implementation of a program of specialized and generic training, treatment and health services. Active treatment does not include services to maintain generally independent residents who are able to function with little supervision or in the absence of a continuous active treatment program."

(2) Administrator- The person who is responsible for the overall management of an ICF/DD licensed under this part and certified under 42 CFR 483 Subpart I. The Administrator must be a Qualified Mental Retardation Professional (QMRP); be a licensed nursing home administrator; have a Bachelor’s degree in a human services field and at least one year of experience working with persons with developmental disabilities or related conditions; or have 5 years’ experience working with persons with developmental disabilities or related conditions.

(3) Advanced Registered Nurse Practitioner (ARNP) - A person duly licensed to practice as an advanced registered nurse practitioner in accordance with Chapter 464, F.S.

(4) Age Appropriate - Services, programming, equipment and supplies that are appropriate for persons who do not have a developmental disability and who are of approximately the same chronological age as the individual.

(5) Certified Behavior Analyst - A person who is certified under the Florida Behavior Certification Program.

(6) Day Program - A program that provides day services for individuals in a non-residential setting. The array of services may include pre-school, pre-vocational and vocational training, behavior management, adult education, recreation, semi-independent and independent skills development training, and individual therapies.

(7) Dental Hygienist - A person duly licensed to practice as a dental hygienist in accordance with Chapter 466, F.S.

(8) Dentist - A person duly licensed to practice dentistry in accordance with Chapter 466, F.S.

(9) Facility - The total administrative unit officially licensed and certified as an ICF/DD, which may consist of a number of living units.

(10) General Supervision – Means the responsible supervision of supportive personnel by a licensed practitioner who need not be present when such procedures are performed, but who assumes legal liability therefor. Except in cases of emergency, “general supervision” must require the easy availability or physical presence of the licensed practitioner for consultation with and direction of the supportive personnel.

(11) Habilitation or Support Plan - A document that identifies the needs of an individual resident; the programs and services to meet those needs; is derived through a joint interdisciplinary, professional diagnosis and evaluation process; and meets the requirements in 42 Code of Federal Regulations (CFR) 483 for an Individual Program Plan (IPP).

(12) Health Care Professional- A physician, physician assistant or advanced registered nurse practitioner.

(13) Interdisciplinary Team (IDT)- The resident or resident’s representative, QMRP, social worker, a licensed nurse responsible for the resident, the resident’s physician and other appropriate staff in disciplines determined by the individual resident’s needs.

(14) Level of Care 7- A level of care code for individuals who have a developmental disability and are in need of ICF/DD placement and are ambulatory or self-mobile using mechanical devices such as canes, walkers, or wheelchairs. These individuals are able to transfer themselves without human assistance.

(15) Level of Care 8 - A level of care code for individuals who have a developmental disability, are in need of ICF/DD placement and who are capable of mobility only with human assistance or need human assistance in order to transfer to or from a mobility device.

(16) Level of Care 9 - A level of care code for individuals who have a developmental disability, are in need of ICF/DD placement, are non-ambulatory and capable of mobility only with human assistance, and require continuous medical/nursing supervision for chronic health problems. Continuous medical supervision means at least monthly observation by a physician or physician's assistant or an advanced registered nurse practitioner (ARNP). That observation must be documented by a progress note entry of the findings, as well as 24 hours per day, seven days per week availability of routine or emergency physician's services. In addition there must be licensed nursing staff on site 24 hours per day, seven days per week.

(17) Licensed Nurse – A person duly licensed to practice nursing as a licensed practical nurse, registered nurse or ARNP in accordance with Chapter 464, F.S.

(18) Licensed Practical Nurse - A person duly licensed to practice as a practical nurse in accordance with Chapter 464, F.S.

(19) Over-the-Counter Medication (OTC) – Medication that is authorized, pursuant to federal or state law, for general distribution and use without a prescription in the treatment of human diseases, ailments, or injuries.

(20) Ophthalmic Medication – Eye solution (eye drops) or ointment to be instilled in the eye or applied around the eyelid.

(21) Oral Medication – Any medication, tablet, capsule, or liquid introduced into the gastrointestinal tract by mouth.

(22) Otic Medication – Solutions or ointments to be applied in the outer ear canal or around the outer ear.

(23) Pharmacist - A person duly licensed to practice pharmacy in accordance with Chapter 465, F.S.

(24) Physician - A person duly licensed to practice medicine in accordance with Chapter 458 or 459, F.S.

(25) Physician’s Assistant - A person duly licensed to practice medicine in accordance with Chapter 458 or 459, F.S.

(26) Prescribed Medication – A drug or medication obtained pursuant to a prescription, as defined in Section 465.003, F.S.

(27) Psychologist - A person duly licensed to practice as a psychologist in accordance with Chapter 490, F.S.

(28) Qualified Mental Retardation Professional (QMRP) - A person who meets the requirements for a qualified mental retardation professional as stated in 42 CFR., Subpart I, Section 483.430.

(29) Registered Dietitian- A person registered by the Commission on Dietetic Registration of the American Dietetic Association.

(30) Registered Nurse (RN) - A person duly licensed to practice as a registered nurse in accordance with Chapter 464, F.S.

(31) Resident - Any person who requires and is receiving active treatment services and residing in an ICF/DD.

(32) Resident Representative - The person authorized or designated to act on behalf of a resident, which includes a guardian, guardian advocate, or other legally appointed representative. May also include a parent or if unavailable another family member.

(33) Restraint - Any device, instrument, manual or chemical method, including an enclosed crib or barred enclosure, used to limit or restrict an individual's movement or normal function of a portion of an individual's body. This definition excludes physical guidance or prompting techniques; response blocking to interrupt an undesired behavior in which physical contact is less than five seconds in duration; devices used to provide support for the achievement of functional body positions and equilibrium that have been prescribed by an appropriate health care professional; devices used as a part of a specific medical, dental or surgical procedure; and standard safety belts used to prevent an individual from falling from a stretcher, wheelchair or vehicle.

(34) Seclusion – When a person is involuntarily confined in a room or a restricted space and is prevented from leaving, or reasonably believes that he or she will be prevented from leaving, by means that include, but are not limited to:

a) Manually, mechanically, or electronically locked doors;

b) One-way doors, that, when closed or unlocked, cannot be opened from the inside;

c) Physical intervention of staff; or

d) Coercive measures, such as the threat of restraint or sanctions, or the loss of privileges that the resident would otherwise have.

(35) Self-Mobile - The ability to use a walker, cane, wheelchair or other mobility device independently without human assistance, including the ability to transfer into and out of the mobility device without human assistance.

(36) Severe Maladaptive Behavior - Actions of an individual that, without environmental, behavioral, physical, or chemical intervention, result in or have the potential to damage the individual or others. Such actions require medical attention or occur with sufficient frequency, magnitude, or duration that a life-threatening situation might result.

(37) Shared Facilities and Services - Those central services or facilities such as food preparation, maintenance, laundry and management that are shared by living units within a facility or with other facilities. This also includes day treatment programs.

(38) Supervision - Directing, overseeing, instructing, monitoring, guiding or evaluating individuals.

(39) Unlicensed Medication Assistant (UMA)–A staff member employed in an ICF/DD who has completed the required medication administration training and has met skills validation requirements for the administration of medications to an ICF/DD resident.

Specific Authority 400.967(2), (c) FS. Law Implemented 400.967(2) FS. History–New________

59A-26.003 License Required.

(1) Before any person or entity may operate an ICF/DD in Florida an application must be made and a license received from the Agency. Successful completion of a licensure survey by the Agency to determine compliance with the requirements of Chapter 400 Part XI, F.S., and this rule must occur prior to issuing a license.

(2) In the case of a facility applying for licensure after purchase of an ICF/DD previously licensed under other ownership, a signed agreement to correct identified licensure and certification deficiencies must accompany the new license application required by 400.962(6), F. S.

(3) When a facility is leased by the real property owner to a second party for operation, the second party must apply to the Agency for a license. A copy of the lease agreement must be filed with the application for a license.

(4) A license shall be valid for a maximum of one calendar year, unless otherwise authorized by statute.

(5) Each licensee must post its license in a prominent place in the facility in clear and unobstructed public view and visible to individuals who are being admitted to the facility.

(6) A license may be suspended, revoked or denied in any case where the Agency finds that there has been substantial failure to comply with:

(a) The provisions of the initial application requirements, certificate of need, the licensure renewal requirements, or the change of ownership requirements;

(b) The certification or re-certification requirements as a Medicaid provider;

(c) Survey standards for ICF/DD licensure; or

(d) Licensure fee requirements.

Specific Authority 400.962 (1), (2) FS. Law Implemented 400.962 (1), (2) FS. History–New________.

59A-26.004 Classification of Deficiencies

Determination by the Agency that conditions or care and treatment at a licensed ICF/DD do not comply with Chapter 400, Part XI or this rule shall be presumed to constitute a deficiency and be classified in accordance with 400.967(3), F.S., unless there is shown clear and convincing evidence to the contrary.

(1) Class I deficiencies are those the Agency determines present an imminent danger to the residents of the facility or a substantial probability that death or serious physical harm would result therefrom. The condition or practice constituting a Class I violation must be abated or eliminated immediately, unless a fixed period of time, as determined by the Agency, is required for correction. A Class I deficiency, is subject to a civil penalty in an amount not less than $5,000 and not exceeding $10,000 for each deficiency. A fine may be levied notwithstanding the correction of the deficiency.

(2) Class II deficiencies are those the Agency determines have a direct or immediate relationship to the health, safety, or security of residents, other than Class I deficiencies. A Class II deficiency, is subject to a civil penalty in an amount not less than $1,000 and not exceeding $5,000 for each deficiency. A citation for a Class II deficiency shall specify the time within which the deficiency must be corrected. If a Class II deficiency is corrected within the time specified, no civil penalty shall be imposed, unless it is a repeated offense.

(3) Class III deficiencies are those the Agency determines to have an indirect or potential relationship to the health, safety, or security of the facility residents, other than Class I or Class II deficiencies. A Class III deficiency, is subject to a civil penalty of not less than $500 and not exceeding $1,000 for each deficiency. A citation for a Class III deficiency shall specify the time within which the deficiency must be corrected. If a Class III deficiency is corrected within the time specified, no civil penalty shall be imposed, unless it is a repeated offense.

(4) As used in this section, repeated offense means a citation for non-compliance with the same regulatory requirement that was previously cited as a Class I, II or III deficiency on or since the last licensure survey, or during the previous 365 days, whichever period is longer.

Specific Authority 400.967(3), (4) FS. Law Implemented 400.967(3), (4) FS. History–New________.

59A-26.005 Licensure Procedure, Fees and Exemptions.

(1) Applicants for initial license must submit to the Agency:

(a) An approved plans review and on-site construction survey showing compliance with 400 Part XI, F.S. and this rule conducted by the Agency and a certificate of occupancy from the local building authority;

(b) A completed licensure application to operate an Intermediate Care Facility for the Developmentally Disabled (ICF/DD), on AHCA Form 3110-5003, November 2004. This form is available from the Agency for Health Care Administration, Long Term Care Unit, 2727 Mahan Drive, MS-33, Tallahassee, Florida, 32308, or from the Agency Web Site at http://ahca.myflorida.com.

(c) The applicant must also submit to the Agency the following items:

1. Licensure fees at the rate of $117.00 per bed by check or money order payable to Agency for Health Care Administration. The licensure fee is not refundable. A license for an initial application will not be issued until the application fee has been received by the Agency and all associated checks have cleared.

2. If the facility is to be managed by an entity other than the licensee, a copy of any and all letters of intent, agreements, memoranda of understanding, or contracts between licensee and management company.

3. An approved fire inspection report from the local fire authority completed no more than three months prior to the date of the initial licensure application received by the Agency.

4. Documentation of compliance with the community residential home requirements specified in Chapter 419, F.S., if applicable.

5. Satisfactory current proof that the applicant possesses the financial ability to operate the facility as demonstrated by bank statements, net worth statements, and audited or reviewed financial statements, all in accordance with Generally Accepted Accounting Principles.

6. A copy of the Certificate of Need issued by the Agency for the facility to be licensed.

7. Proof of the licensee’s current right to occupy the ICF/DD building, such as, a copy of a lease, sublease agreement or deed.

(2) Applicants applying for renewal of a license must submit:

(a) A completed application on AHCA Form 3110-5003, November 2004. Form available from the Agency for Health Care Administration, Long Term Care Unit, 2727 Mahan Drive, MS-33, Tallahassee, Florida 32308, or from the Agency Web Site at http://ahca.myflorida.com. The application must be postmarked no later than 90 days prior to expiration of the license. If no postmark is available, the application must be received by the Agency 90 days prior to expiration. Failure to timely file a renewal application is punishable by a late fine equal to one half the licensure fee in effect at the time of application.

(b) Licensure fees at the rate of $117.00 per bed by check or money order payable to the Agency for Health Care Administration. The licensure fee is not refundable. If a check for the renewal licensure fee is dishonored and returned to the Agency, the license holder will have 10 calendar days to pay the full amount plus any applicable fees as provided by law. Such payment must be made by cash, cashiers check, or money order. Failure to pay the licensure and processing fee will result in suspension of the license until all fees are paid in full.

(c) If changes have occurred in the management of the licensee between licensure periods the facility must report those changes to the Agency at the time of its renewal application, and provide a copy of any and all letters of intent, agreements, memoranda of understanding, or contracts between licensee and management company.

(3) Applicants applying for a change of ownership must submit:

(a) An application for licensure on AHCA Form 3110-5003, November 2004. Form available from the Agency for Health Care Administration, Long Term Care Unit, 2727 Mahan Drive, MS-33, Tallahassee, Florida 32308, or from the Agency Web Site at http://ahca.myflorida.com. The application must also include the licensure fees postmarked no later than 90 days prior to the date the change of ownership becomes effective. If no postmark is available, the application must be received by the Agency 90 days prior to the date the change of ownership becomes effective. Failure to timely file a change of ownership application is punishable by a late fine equal to one half the licensure fee in effect at the time of application. A license for a change of ownership application will not be issued until the application fee has been received by the Agency and all associated checks have cleared.

(b) All documents and fees required for initial licensure in (1) of this section, with the exception of (1) (a), (1) (c) 3, 4, and 6.

(c) A signed agreement to correct all outstanding licensure and certification deficiencies incurred by the previous licensee in accordance with the previously approved plan of correction.

(4) After determination of compliance with this rule and Chapter 400, Part IX, F.S., a license to operate an ICF/DD may be issued by the Agency.

Specific Authority 400.962 (1), (2) FS. Law Implemented 400.962 (1), (2) FS. History–New________.

59A-26.006 Responsibilities for Operation.

(1) The licensee must be in compliance with all conditions and standards in Title 42, Code of Federal Regulations 483 Subpart I sections, 483.410 through 483.480, Requirements for Intermediate Care Facilities for Persons with Developmental Disabilities. The licensee must ensure compliance with state regulations in Chapter 409, F.S., and applicable rules as a provider of Medicaid services to persons who are mentally retarded or who have related conditions as stated in Title 42, Code of Federal Regulations.

(2) Within 60 days of initial licensure the licensee must be certified in accordance with federal regulations as stated in Title 42, Code of Federal Regulations, 483 Subpart I sections, 483.410 through 483.480.

Specific Authority 400.967(1), (2) FS. Law Implemented 400.967(1), (2) History–New________.

59A-26.007 Fiscal Standards.

The licensee must maintain fiscal records in accordance with Generally Accepted Accounting Principles, Chapter 400 Part XI, F.S., Chapter 409 and applicable rules. There must be a recognized system of accounting used to accurately reflect details of the ICF/DD operation, including residents' funds held in trust and other resident property. The fiscal and resident fund records must be supported by adequate documentation of all transactions. Documentation of quarterly reconciliation for resident fund records must be kept on file for five years, and must be provided to the Agency for review when requested. The licensee must:

(1) Operate the facility on a sound financial basis consistent with good business practices. Evidence of issuance of bad checks or accumulation of delinquent bills for such items as personnel salaries, contracted services, food, drugs or utilities shall constitute prima facie evidence that the ownership lacks satisfactory financial management skills or resources to operate the ICF/DD in accordance with the requirements of Section 400.962, F.S., and this rule. The issuance by the licensee of 6 or more worthless checks during a 90 day period, whether or not there has been a prosecution under Section 831.09, F.S., or the accumulation of delinquent bills in an amount in excess of $2,500 for which the licensee is primarily obligated, shall create a rebuttable presumption that the facility is not being operated on a sound financial basis. Within 10 calendar days of the receipt of notification for this presumed fiscal deficiency, the licensee may rebut to the Agency by clear and convincing evidence that the facility has the requisite financial basis necessary to avoid revocation, and denial of licensure.

(2) Refund any amount or portion of prepayment in excess of the amount or portion obligated for services already furnished if a resident leaves the facility prior to the end of any prepayment period.

(3) Maintain financial and statistical records in accordance with Title 42 CFR, Sections 413.24 (a), (b), (c) and (e). The licensee is required to detail all of their costs for their entire reporting period making appropriate adjustments for determination of allowable costs as required by the Florida Title XIX Intermediate Care Facility for the Mentally Retarded and Developmentally Disabled Reimbursement Plan for Not Publicly Owned and Operated or Publicly Owned and Operated Facilities. The cost report must be prepared using accrual basis of accounting in accordance with Generally Accepted Accounting Principles, as incorporated by reference in Rule 61H1-20.007 F.A.C., the methods of reimbursement in accordance with Medicare (Title XVIII) Principles of Reimbursement, the Provider Reimbursement Manual CMS PUB. 15-1, incorporated by reference in Rule 59G-6.010, F.A.C, except as modified by the Florida Title XIX Intermediate Care Facility for the Mentally Retarded and Developmentally Disabled Reimbursement Plan for Not Publicly Owned and Operated or Publicly Owned and Publicly Operated facilities, and State of Florida Administrative Rules.

(4) Submit to any audit when deemed necessary by the Agency to ensure the facility is in full compliance with Chapter 400, Part XI, F.S., and this rule. The licensee must maintain copies of facility billings and payment records on the premises or must have these records available for inspection and copying within seven calendar days of notice by the Agency if not maintained on the premises.

(5) Keep complete and accurate records of all residents' funds, other effects, and property.

(6) Deposit and maintain in an interest bearing account with a financial institution on behalf of each resident, all money and interest on money held for that resident. A copy of the resident’s bank account statements and expenditure detail must be provided to the resident or resident’s representative within seven calendar days of written request.

(7) Protect residents’ funds from theft, negligence or abuse. Should loss of a resident's funds occur, the licensee will be responsible for reimbursing the resident for the full amount of funds to which he or she is entitled within 30 calendar days of confirmation of the theft, negligence or abuse of resident funds.

(8) Make a final accounting of all personal effects and money belonging to the resident held by the licensee upon the discharge or death of a resident within 30 calendar days after the resident’s discharge or death.

Specific Authority 400.967 (2)(e), FS. Law Implemented 400.967 (2)(e) FS. History–New________.

59A-26.0075 Fiscal Prohibitions, Kickbacks, and Referrals

The licensee, administrators, consultants, and employees are prohibited from:

(1) Paying any commission, bonus, rebate or gratuity to any organization, agency, health care provider or other person for referral of any resident to the facility;

(2) Requesting or accepting any remuneration, rebate, gift, benefit, referral of other business, or advantage of any form from any vendor or other supplier because of the purchase, rental or loan of equipment, supplies or services for the facility or resident, not consistent with normal business practice.

Specific Authority 400.967(2)(e) FS. Law Implemented 400.967(2)(e) FS. History–New________.

59A-26.008 Admission Policies and Requirements.

(1) The admission of an individual to an ICF/DD must be under the supervision of the administrator of the facility.

(2) Individuals shall only be admitted after completion of a written admission agreement, which shall constitute a contract between the licensee and resident. The agreement must be in effect at all times while the individual is a resident of the facility. The agreement must be reviewed annually for revisions by the licensee and the resident, or resident’s representative. Either party may initiate revision to the agreement at any time or when substantial changes in the resident’s condition occur. No agreement or any provision thereof shall be construed to relieve any licensee of any requirement or obligation imposed upon it by 400 Part XI, F.S. and this rule. Such agreements must be maintained by the licensee for at least five (5) years after each resident’s expiration or discharge from the facility, whichever is sooner, and assess no additional charges, expenses or other financial liabilities in excess of the provisions included in the admission contract. All charges for services not covered by Title XIX of the Social Security Act or not covered by the basic per diem rates of the licensee, for which the resident or the resident’s representative may be responsible for payment must be specified in the admission contract.

(3) The licensee must comply with the admission agreement. The admission agreement must include a description of the program and services to be provided, including at a minimum:

(a) The daily, weekly, or monthly rate, and refund provisions for unused portions thereof;

(b) Board;

(c) Lodging;

(d) Residential and nursing services;

(e) Linen and furnishings as required;

(f) Sufficient seasonal clothing as required by the resident, and applicable to the resident’s needs, when the resident, or resident’s representative does not provide sufficient clothing. Sufficient seasonal clothing must be provided and include a basic wardrobe as required by the individual, including a five-day supply of sleepwear, socks, shoes, undergarments, outer clothing such as shirts, pants, or dresses, a winter coat, raingear, and personal grooming and hygiene items. The licensee must maintain an inventory of the resident’s clothing, and provide a copy of the inventory to the resident or resident’s representative within seven calendar days of a written request;

(g) Training and assistance as required with activities of daily living;

(h) The provision and maintenance of walkers, wheelchairs, dentures, eyeglasses, hearing aides and other orthotic, prosthetic or adaptive equipment as prescribed;

(i) Therapies prescribed by the resident’s individual habilitation or support plan including medical and nutritional therapies;

(j) Transportation services including vehicles with lifts or other adaptive equipment when needed;

(k) Other services prescribed in the resident’s individual habilitation or support plan; and

(l) Provisions for providing a duplicate of the agreement to the resident or resident’s representative.

(4) The following conditions apply to admission and retention of all residents:

(a) Individuals must not be admitted to or retained in a facility if the licensee cannot provide, or arrange for the provision of all services prescribed in the individual habilitation or support plan.

(b) Residents who have been voluntarily admitted must not be held in a facility against their will.

(c) The licensee must develop procedures to be implemented in the event that a voluntarily admitted resident should decide to leave the facility against the recommendations of the interdisciplinary team. Procedures must include:

1. Counseling by the facility social worker or QMRP with referrals made to the Agency for Persons with Disabilities and other professionals or advocates, as appropriate.

2. If a resident persists in leaving, the licensee will assist the resident in locating an appropriate alternative placement.

(5) Individuals who have a communicable disease must be evaluated by a physician prior to admission. If the physician’s evaluation finds the disease would endanger other residents of the facility, the admission should be postponed until the communicable period has passed or appropriate precautions have been implemented by the facility staff.

(6) A registered nurse must assess each newly admitted resident within four (4) hours after admission.

(7) If a pre-existing medical condition exists, if medical problems are identified by the nursing admissions assessment, or if a resident is admitted who does not have a complete medical record including medical history, positive physical findings, diagnosis, and signed physician’s orders for treatment, nursing care or diets, the resident must be examined by the admitting physician within 96 hours of admission unless the registered nurse determines that the physician should examine the resident sooner.

Specific Authority 400.967(2)(f) FS. Law Implemented 400.967(2)(f) FS. History–New________.

59A-26.009 Personnel Standards.

(1) Each new staff employed by the facility to provide direct services to residents must have a medical examination at the time of employment and prior to contact with residents. Annually thereafter, staff must submit a physician's statement that based on test results, the employee does not constitute a threat of communicating diseases to residents. If any staff is found to have or is suspected of having a communicable disease, he or she must be removed from all duties that require contact with residents until certification is received from a physician that such risk no longer exists.

(2) All staff or prospective staff of the facility that are expected to be or whose responsibilities are such that they would be considered to be a direct service provider will have a Level 2 background screening as provided in chapter 435, F.S. Facilities must have in their possession evidence of compliance with Level 2 background screening requirements before allowing an employee to begin working with residents.

(3) Licensees must comply with the requirements of Chapter 435, Employment Screening and ss. 400.964, Florida Statutes.

(4) Regardless of the organization or design of resident living units, the minimum overall direct care staff-resident ratios must comply with those specified in 42, Code of Federal Regulations 483.430(d)(3).

(5) The licensee must have an administrator, sufficient licensed nurses to care for each resident’s health care needs, and a sufficient number of Qualified Mental Retarded Professionals to ensure each resident’s active treatment program is integrated, coordinated and monitored.

(6) All staff must complete and pass an educational course biennially on human immunodeficiency virus (HIV) and acquired immune deficiency syndrome (AIDS) as described in Chapter 381.0035, F.S.

(a) This course will have no less than two contact hours of training.

(b) Confirmation of completion of such course must be maintained in facility records for the duration of employment and for 1 year after separation of employment.

(c) All new staff must complete and pass an education course on HIV and AIDS within 90 days of employment as described in Section 381.0035, F.S.

(7) All staff must receive training within 30 days of employment and annually thereafter on the licensee’s emergency disaster procedures that include the staff’s role before, during, and after the emergency.

(8) The licensee must ensure 50% of their staff on duty at all times are certified in cardio-pulmonary resuscitation (CPR) and have received basic first aid training.

(9) All staff must receive training and demonstrate competency in the prevention and minimal use of restraint and seclusion within 30 days of employment. Competency in these methods must be demonstrated and documented annually thereafter.

(a) Training must include at a minimum:

1. The emotional and physical effects of restraint and seclusion on residents and staff.

2. History of trauma, impact on residents and the potential for retraumatization.

3. Crisis prevention and intervention approaches including de-escalation strategies.

4. Applicable legal and clinical requirements governing behavioral services, restraint and seclusion.

5. Safe and appropriate initiation of physical contact and application and monitoring of restraint and seclusion.

6. Approaches to facilitate the earliest possible release from restraint or seclusion.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(b) FS. History–New________.

59A-26.010 Training, Habilitation, Active Treatment, Professional, Special Programs and Services.

(1) Programs, services, functions and the pattern of staff

organization within the facility must be focused upon serving the individual needs of each resident and must provide for:

(a) Comprehensive diagnosis and evaluation of each resident as a basis for planning, programming and managing such that the assessment of each resident’s abilities, preferences, needs, behavior assessment, behavior intervention plan and level of functioning is comprehensive in scope and adequately addressed in the habilitation plan or support plan.

1. The QMRP is responsible for the integration, coordination, monitoring and review of each resident’s active treatment program, which may require the involvement of other personnel, including other agencies serving the resident.

2. For school age residents when services are provided by the local school district, the licensee must make regular and consistent efforts to include the school system, the resident, and resident’s representative, when practicable in the habilitation planning process. The licensee’s individual program plan shall be in addition to any individual education plan prepared by the school district.

(b) Freedom of movement consistent with the protection of the health, safety, and welfare of individual residents within and outside of the facility.

(c) Routine and ongoing monitoring of each resident’s conditions for early detection of health or nutrition risks which, when found, must be analyzed by the interdisciplinary team to identify probable causes and to implement appropriate intervention strategies.

(d) Recognition and resolution of resident care problems through appropriate participation of professional staff and consulting personnel.

(e) Consideration of every reasonable alternative, least restrictive and most effective procedures, prior to the use of invasive treatment.

(f) Proper, routine positioning of residents who cannot position themselves in appropriate body alignment.

(g) Documented and observable evidence of progress that each resident demonstrates in attaining goals and objectives specified in the habilitation plan, support plan or individual program plans.

(h) Each resident’s active treatment program plan must be reviewed and revised by the interdisciplinary team as necessary:

1. At least annually.

2. When there is a substantial reduction of active treatment or routine physical care in response to health care needs as indicated by a loss of acquired skills or significant worsening of undesirable behavior.

(i) All residents shall have the opportunity to eat orally and receive therapeutic services necessary to maintain or improve eating skills and abilities, unless this is not possible as assessed by the interdisciplinary team. For residents who receive enteral and/or parenteral feedings, the interdisciplinary team must evaluate and review these residents’ potential to return to oral eating at least quarterly.

(j) Resident rights as provided in the Bill of Rights of Persons Who Are Developmentally Disabled, Section 393.13 (3)(a)-(j), F.S.

(k) Equipment essential to ensure the health, safety and welfare of each resident.

(2) Staff responsible for providing resident care must be proficient in the physical and nutritional management skills appropriate to the residents served.

(3) The licensee must provide instruction, information, assistance and equipment to help ensure that the essential physical and nutritional management of each resident is continued in educational, day treatment and acute care facilities.

(4) For facilities licensed for six beds or less, active treatment in the form of day treatment program activities must be provided in an off-site community setting unless medically contraindicated due to a resident’s acute health problem or contraindicated for the resident as determined by the interdisciplinary team including the resident’s physician. For facilities licensed for more than 6 beds, active treatment in the form of day program activities will be provided off-site or at a physical location other than the living unit unless medically contraindicated due to a resident’s acute health problem or contraindicated for the resident as determined by the interdisciplinary team including the resident’s physician. Examples of active treatment include training in personal skills essential for privacy and independence, toileting, personal hygiene, dental hygiene, self-feeding, bathing, dressing, grooming and communication of basic needs.

(5) Licensed practical nurses working in an ICF/DD must be supervised by a registered nurse, ARNP or physician. Nursing physical assessments must be conducted by a registered nurse, ARNP or physician.

(6) Nursing service documentation in resident records must include a comprehensive nursing assessment and, as appropriate, medications, treatments, dietary information, and other significant nursing observations of resident conditions and responses to resident programs. For those residents with stable conditions, nursing progress summaries are adequate in leu of shift documentation, as long as significant events are also recorded.

(7) Standing orders for medications, and pro re nata (p.r.n. or "as needed") orders are prohibited for the use of psychotropic medication including hypnotics, antipsychotics, antidepressants, antianxiety agents, sedatives, lithium, and psychomotor stimulants. The resident’s physician must review medication orders at least every 60 calendar days except for residents having a Level of Care 9, in which case medication orders must be reviewed by the physician at least every 30 calendar days.

(8) For residents using medication to manage behavior, their individual program plan must specify observable and measurable symptoms to be alleviated by the medication, intervals for re-evaluating the continued use of the medications by the interdisciplinary team and consideration of the reduction and elimination of the medication.

(9) When a psychotropic medication is initiated, based upon a recommendation by the interdisciplinary team, a physician, ARNP, registered nurse or pharmacist must assure or make provisions for the instruction of the facility staff regarding side effects and adverse effects of the prescribed medication including when to notify the physician if undesirable side effects or adverse effects are observed. The staff must document in the progress notes that these instructions have been given. Any time a psychotropic medication is initiated, changed, increased or decreased, the physician must write a progress note. At a minimum the physician must make a progress note every 30 calendar days. The effect of the medication on targeted symptoms must be reviewed and monitored at least quarterly by the IDT.

(10) Psychologists or certified behavior analysts must provide regular and ongoing consultation and in-service training to staff concerning:

(a) Principles and methods of understanding and changing behavior in order to devise the most optimal and effective program for each resident.

(b) Principles and methods of individual and program evaluation, for the purposes of assessing resident response and measuring program effectiveness.

(c) Design, implementation and monitoring of behavioral services.

(11) If a physical or mechanical restraint is used on a resident, the resident must be placed in a position that allows airway access and does not compromise respiration. Airway access and respiration must not be blocked or impeded by any material placed in or over the resident’s mouth or nose. A resident must be placed in a face-up position while in restraints. Hand cuffs or shackles must not be used for the purposes of restraints.

(12) The licensee must develop and implement policies and procedures to reduce, and whenever possible, eliminate the use of restraints and seclusion. Policies must include:

(a) Debriefing activities as follow up to use of restraints and seclusion.

(b) A process for addressing resident concerns and complaints about the use of restraint and seclusion.

(c) A process for analyzing and identifying trends in the use of restraint and seclusion.

(13) Recreation required by each resident's habilitation plan or support plan must be provided as a purposeful intervention, through activities that modify, ameliorate, or reinforce specific physical or social behaviors.

(14) Leisure activities for residents for whom recreation services are not a priority in the resident individual program plan, must be provided in accordance with individual preferences, abilities, and needs, and with the maximum use of community resources.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(d), (f) FS. History–New________.

59A-26.011 Dietary Services.

(1) All dietary services must have oversight by and medical nutritional therapy must be provided by a registered dietician, employed full time, part time or on a consultant basis.

(2) There must be sufficient, competent staff responsible for food preparation and service.

(3) Menus must be prepared in advance, followed and made accessible to residents and staff.

(4) Menus must be approved by the registered dietitian.

(5) Each resident must receive food prepared by methods that conserve nutritive value, flavor and appearance.

(6) Each resident must receive food that is palatable, attractive and at the proper temperature.

(7) Substitutes offered must be of similar nutritive value.

(8) All matters pertaining to food service must comply with the following regulations based on the number of beds to be licensed:

(a) For facilities with 25 or more beds the provisions of Chapter 64E-11, F.A.C., Florida Hygiene Code, shall apply.

(b) For facilities with 24 beds or fewer the provisions of Chapter 64E-12, F.A.C., Community Based Residential Facilities, as enforced by the Department of Health, shall apply. The Agency will refer suspected food safety issues to the Department of Health.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(f) FS. History–New________.

59A-26.012 Dental Services.

(1) Comprehensive dental diagnostic services must be provided to all residents and must include:

(a) Periodic, at least annual, oral prophylaxis, by a dentist or dental hygienist; and

(b) At least annually, a complete extra and intra oral examination utilizing diagnostic aides necessary to properly evaluate each resident’s oral condition.

(2) Comprehensive dental treatment services must be provided to all residents and must include:

(a) Daily oral care, as prescribed by a dentist or dental hygienist; and

(b) Emergency treatment on a 24-hour, seven days-a-week basis, by a dentist and;

(c) Treatment as prescribed by a dentist.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(f) FS. History–New________.

59A-26.013 Psychological Services

Psychologists providing services to the residents of the facility must be licensed pursuant to Chapter 490.005, F.S. and have experience or training in the field of mental retardation.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(f) FS. History–New________.

59A-26.014 Drugs and Pharmaceutical Services.

(1) An ICF/DD must have a Class I Institutional Pharmacy Permit as defined in Section 465.019, F.S. All prescription medications must be compounded and dispensed by a pharmacy registered in Florida.

A consultant pharmacist must be responsible for implementation of the pharmacy program as defined by each licensee even when the consultant pharmacist is not the vendoring pharmacist.

(2) Labeling of prescription medications must be in accordance with Chapters 465 and 499, F.S., and Chapter 64B-16, F.A.C. Stock bottles of nonprescription drugs which are properly labeled according to the regulations related to the Drug and Cosmetic Act, Chapter 499,F.S., are permitted.

(3) All drugs including nonprescription stock drugs must be stored in a locked room or cabinet, or in a locked drug cart. External medications must be stored separately from internal and ophthalmic preparations. Poisons must be separated from all other drugs.

(4) Biologicals and other drugs must be stored in accordance with the current U.S. Pharmacopoeia. If refrigeration is required these drugs must be in a locked container.

(5) All drugs listed in Schedules II through V must be handled, used, administered and dispensed in accordance with the Comprehensive Drug Abuse Prevention and Control Act of 1970, 21 U.S.C., related regulations, and Chapter 893, F.S. The Drug Abuse Prevention and Control Act can be located at the following web address: www.usdoj.gov/dea/agency/csa.htm or by mail at Drug Enforcement Administration Office of Diversion Control (ODLP) Washington, D.C. 20537.

(6) A count of controlled drugs listed in Schedules II-V of the Drug Abuse Prevention and Control Act, and Chapter 893, F.S., must be made jointly between shifts by the licensed nurse beginning duty and the licensed nurse leaving duty. For facilities licensed for six beds or less, the count must be done by the supervising registered nurse on a weekly basis. For facilities licensed for more than six beds, a medication count of controlled substances must be made at every change of shift by the licensed nurse or an unlicensed medication assistant as defined in this rule. The count at shift change must be witnessed by another licensed nurse or another staff member trained in medication administration.

(7) A registry must be maintained for all drugs listed in Chapter 893, F.S. as Schedules II, III, IV, and V for continuous reconciliation.

(8) Medicinal substances classified as controlled substances by the Drug Enforcement Administration (DEA), as provided in the Drug Abuse Prevention and Control Act of 1970 and related regulations, and the Drug Abuse Prevention and Control Act in Chapter 893, F.S. and related regulations must be disposed of in accordance with Chapter 64B-16, F.A.C.

(9) Disposal of other drugs not covered above must be made in accordance with an organized system of drug administration.

(10) All prescribed drugs dispensed for the resident while in the facility may be given to the resident or resident’s representative upon discharge with the physician’s written orders.

(11) An inventory of drugs released must be prepared and signed by the licensed nurse releasing the drugs and the person receiving the drugs. This inventory must be filed in the resident’s medical record.

(a) All medications of deceased residents must be accounted for on an inventory list prepared by a licensed nurse and filed in the resident’s record. These medications must be returned for credit or destroyed in accordance with this section.

(b) All controlled drugs not administered to a resident due to wastage, loss, or returned to the pharmacy must be documented in each resident’s medical record and accounted for by two licensed nurses, and in accordance with the DEA Compliance Policy Guidelines for Disposal of Controlled Substances, CFR 21, Title 21, Section 1307.21, Disposal of Controlled Substances.

(12) All verbal orders must be written on the physician’s order sheet by the licensed nurse receiving the order and countersigned by the physician within 72 hours. Verbal orders for Schedule II drugs are permitted only in emergency situations. In an emergency situation, the physician must directly contact the pharmacist and the pharmacist must receive a copy of the original or direct copy of the physician’s order within 72 hours.

(13) Telephoned physician orders for medication may only be accepted by a licensed nurse, a physician’s assistant or a licensed pharmacist. Telephoned orders will be immediately recorded in the resident’s medical record. Faxed physician orders are acceptable with a physician’s signature. A physician’s signature on the original physician’s order must occur within 72 hours of receipt of the faxed order.

(14) Emergency medication kits used by facilities must adhere to the following:

(a) The physician, pharmacist, and registered nurse must select drugs and ancillary equipment to be included in the emergency medication kit.

(b) The kit must be maintained and safeguarded in accordance with federal and state laws and regulations pertaining to the specific drug items included.

(c) The kit must be secured at all times.

(d) The consultant pharmacist must be responsible to assure that all drug items have not expired and are properly labeled, controlled, and stored in a sealed container.

(e) When the seal is broken for any reason, the pharmacy must be notified immediately and must provide the facility with a new emergency medication kit, or the necessary medications to replenish the kit by the next business day. Following removal of an item from the kit, the kit must be resealed. Only the pharmacist or the licensed nurse will check the contents, replace necessary items and reseal the kit if a new kit is not provided.

Specific Authority 400.967 FS., 400.9685 FS. Law Implemented 400.967(f) FS. History–New________.

59A-26.015 Administration of Medications to ICF/DD Residents by Unlicensed Medication Assistants.

(1) It is the responsibility of the licensee to ensure that individual unlicensed medication assistants (UMA) who will be administering medication to residents meet all requirements of this rule.

(2) Unlicensed medication assistants may administer only prescribed, prepackaged, premeasured oral, topical nasal and ophthalmic medications.

(3) Unlicensed medication assistants may administer Over The Counter (OTC) medications including; acetaminophen, cough medicine, antihistamines or decongestants, as currently prescribed by the resident’s health care professional.

(4) Unlicensed medication assistants may not administer medications by injection including intra-muscular, intravenous or subcutaneous, nor any medication administered vaginally or rectally.

(5) Unlicensed medication assistants may administer medications to a resident after the following requirements are met for that resident:

(a) A current informed consent has been signed by the resident, or resident’s representative. The consent must acknowledge and permit unlicensed medication assistants to administer specifically listed medications currently prescribed by a licensed health care professional to the resident. The informed consent must be updated and signed at least annually.

(b) A written report for each resident assisted that indicates the resident’s behavior and any past medication reactions must be documented on the Medication Administration Record (MAR), and updated if the resident’s behavior or medication reactions change. Information regarding this report can be provided by the resident or resident’s representative, or another unlicensed medication assistant or direct care staff person who is familiar with the resident. The person administering medications must be aware of this information prior to administering medications to residents.

(c) A determination is made that the resident to whom medication will be administered has not been deemed to be capable of the safe handling of his or her own medications by his or her primary care doctor.

(6) Administration of medication by unlicensed medication assistants must be under the supervision of a registered nurse or ARNP.

(a) Supervision includes weekly monitoring of medication and 24-hour availability via telephone or paging device by a registered nurse or ARNP.

(b) Prior to assigning tasks to an unlicensed medication assistant, the supervisory nurse must verify the training and validation of the unlicensed medication assistant as required by this rule.

(c) The supervisory nurse must communicate the assignment to the unlicensed medication assistant and verify the unlicensed medication assistant’s understanding of the assignment.

(d) Monitoring and supervision of the completion of the assignment must be documented by the supervising nurse.

(e) The supervising nurse must participate in performance evaluations of the unlicensed medication assistant relative to performance of medication administration.

Specific Authority 400.967 FS., 400.9685 FS. Law Implemented 400.9685 FS. History–New________.

59A-26.016 Requirements for Administration of Medication to Residents by Unlicensed Medication Assistants.

(1) General considerations governing administration of medication:

(a) Outdated medication must be properly destroyed by the supervising nurse. The disposal will be witnessed by one other staff of the facility and a record of the medication disposal must be maintained by the facility and signed by the supervising nurse and witness.

(b) Torn, damaged, illegible or mislabeled prescription labels should be reported immediately to the dispensing pharmacy or pharmacist.

(c) Residents must not miss medications due to delays in refilling a prescription. It shall be the responsibility of the supervising nurse to ensure that refills are ordered and obtained in a timely manner.

(d) No resident shall be administered a prescription or Over the Counter(OTC) medication or treatment, except upon the written order of the resident’s prescribing health care professional.

(2) The following duties must be performed by the unlicensed medication assistant when administering medications to residents. The unlicensed medication assistant must:

(a) Wash his or her hands with soap and water prior to administration of medication, or supervising the self-administration of medication to residents. Unlicensed assistive staff will also wash their hands between the administration of medication to each resident and when there is a change in route of administration.

(b) Prepare medications for one individual resident at a time, in a quiet location that is free from distraction.

(c) Administer medications to one resident at a time. To complete a resident’s medication process, the medication of one resident must be returned to the portable or permanent medication storage unit before administering medications to, or supervising the self-administration of medication for another resident.

(d) Administer medications to each resident, at the time, with the dosage, and by the route prescribed by the resident’s health care professional. Each time medication is administered:

1. Conduct a triple-check of the dosage and time of administration against the original medication container label and the MAR before administering or supervising the self-administration of the medication;

2. Confirm the resident to whom the medication is to be administered is the same resident for whom the medication has been prescribed or ordered;

3. Administer as prescribed and via the route instructed by the resident’s prescribing health care professional;

4. Do not crush, dilute or mix medications without written directions or instructions from the resident’s prescribing health care professional.

5. Check the expiration date before administering each medication. Medications with an expiration date preceding the current date will not be administered.

6. If the resident requires specific positioning or the use of special techniques to facilitate ingestion, including swallowing, all unlicensed medication assistants responsible for administering medication or supervising the administration of medication for that individual must facilitate the correct positioning and use any adaptive equipment required for the proper administration of medications.

(e) Ensure the oral medication administered or supervised during self-administration has been completely ingested before leaving the resident. Directly observe the resident for a period of at least twenty minutes following the administration of a new medication ordered by the resident’s prescribing health care professional. This observation period is to immediately detect and react to possible side-effects of the medication or to document the effectiveness of the medication. Unlicensed medication assistants must review the MAR for special instructions regarding required observation of medications and the unlicensed medication assistant must continually monitor for side-effects and effectiveness of all administered drugs.

(f) The documentation of each medication administered to a resident must be recorded immediately in the MAR by the unlicensed medication assistant administering the medication.

Specific Authority 400.967, 400.9685 FS. Law Implemented 400.9685(3) FS. History–New________.

59A-26.017 Training and Validation Required for Unlicensed Medication Assistants.

(1) Required medication administration training must provide instruction and training, including criteria to ensure that competency is demonstrated through validation of the unlicensed medication assistant after completing the medication administration training. Training and instruction must include all requirements of unlicensed medication assistants listed in this rule.

(2) Medication administration training will be conducted by a registered nurse, ARNP or physician for unlicensed medication assistants and will be provided by the ICF/DD licensee. Trainer orientation sessions will include current requirements of this rule and information to be covered during medication administration training sessions. Any person providing medication administration training sessions or conducting skills validation tests must first complete a trainer orientation session. Documentation of the trainer’s completed orientation will be provided to each unlicensed medication assistant that he or she trains or validates.

(3) The required medication administration training must include the following topics:

(a) Basic knowledge and skills necessary for medication administration charting on the Medication Administration Record (MAR).

(b) Roles of the physician, nurse, pharmacist and direct care staff in medication supervision.

(c) Procedures for recording/charting medications.

(d) Interpretation of common abbreviations used in administration and charting of medications.

(e) Knowledge of facility medication system.

(f) Safety precautions used in medication administration.

(g) Methods and techniques of medication administration.

(h) Problems and interventions in administration of medications.

(i) Observation and reporting of anticipated side effects, adverse effects and desired positive outcome.

(j) Each duty of unlicensed medication assistants as required in this rule.

(4) Validation of competency of the training is required for each unlicensed medication assistant. To become validated, the unlicensed medication assistant must be able to successfully demonstrate, in a practical setting, his or her ability to correctly administer or supervise the self-administration of medications to a resident in a safe and sanitary manner and to correctly and accurately document actions related to the administration of medications, in accordance with the requirements of this rule. At completion of the training an unlicensed medication assistant must attain an overall score of 100% on knowledge tests that cover the training and facility specific questions. The unlicensed medication assistant will have 3 attempts to achieve a 100% score, if after the 3rd attempt a score of 100% is not achieved the unlicensed medication assistant must repeat the training, and may not administer medication to residents until such time as a score of 100% is achieved. Additionally, an unlicensed medication assistant must be able to state the purpose, common side effects, and signs and symptoms of adverse reactions for a list of commonly used medications included in information provided at the medication administration training from memory or demonstrate how they obtain that information and maintain it for easy access.

(5) Validation testing for the administration training curriculum will be conducted by a RN, physician, or ARNP. The ICF/DD licensee will maintain documentation containing the following information:

(a) The name and address of the validator.

(b) Validation date, with expiration date of 365 days from the validation.

(c) Printed name and signature of the validating health care professional, as it appears on his or her license; and

(d) Validating health care professional’s license number, with license expiration date.

(6) All training curricula, handouts, testing materials, and documents used to comply with the medication administration training and skills requirements of this rule will be kept on file in the ICF/DD facility.

(7) The following must be validated for each unlicensed medication assistant:

(a) Demonstration of the ability to read and follow medication instructions on a prescription label, physician’s order or MAR.

(b) Demonstration of the ability to write legibly, complete required documentation, and convey accurate and discernable information.

(c) Demonstration of the ability to perform as required in this rule.

(8) Unlicensed medication assistants and the ICF/DD licensee must maintain a copy of the unlicensed medication assistant’s current skills validation document, and documentation of orientation for their medication administration trainer and validator. Unlicensed medication assistants are responsible for maintaining a copy of these documents and providing copies to the ICF/DD licensee if requested.

(9) Unlicensed medication assistants will have available a copy of their signed skills validation documentation to provide to the resident or resident’s representative if requested. Unlicensed medication assistants will also have available if requested a copy of their annual skills revalidation documentation, within five working days of the revalidation date.

(10) Unlicensed medication assistants who have not successfully renewed their validation prior to the expiration date will not be eligible to administer medications to residents until medication administration retraining and revalidation of skills have been successfully completed.

Specific Authority 400.967 FS., 400.9685 FS. Law Implemented 400.9685 FS. History–New________.

59A-26.018 Plant Maintenance and Housekeeping.

(1) The facility must maintain the interior and exterior of buildings accessible to residents and all equipment, furniture, and furnishings in a clean and good working condition such that resident safety and well-being are not jeopardized.

(2) Each licensee must establish written policies designed to maintain the physical plant and overall ICF/DD environment in such a manner that the safety and well-being of residents are ensured. The building and mechanical maintenance program must be under the supervision of a qualified person, as determined by the facility. All mechanical and electrical equipment must be maintained in working order, and must be accessible for cleaning and inspecting. All mechanical systems must be tested, balanced and operated prior to being placed into service and maintained in good working order. The facility must have an effective written plan for maintenance, including record keeping, sufficient staff, appropriate equipment and adequate supplies. The facility must:

(a) Maintain the building in good repair, safe and free of the following: cracks in the floors, walls, or ceilings; peeling wallpaper or paint; warped or loose boards; warped, broken, loose, or cracked floor covering, such as tile, linoleum or vinyl; loose handrails or railings; loose or broken window panes and screens; and other similar hazards.

(b) Maintain all electrical, lighting (interior and exterior), signal, mechanical, potable water supply, hot water heaters, heating, air conditioning, fire protection and sewage disposal systems in safe, clean and functioning condition.

(c) Maintain all electrical cords and appliances in a safe and functioning condition.

(d) Maintain the interior and exterior finishes of the buildings as needed to keep them attractive, clean, and safe, to include painting, washing, and other types of maintenance.

(e) Maintain all furniture and furnishings in a clean, attractive and safe condition.

(f) Maintain the grounds free from refuse, litter, insect and vermin breeding areas.

(g) Maintain screens on windows and doors in good repair, free of breaks in construction.

(3) The facility must have an effective plan for housekeeping including sufficient staff, appropriate equipment and adequate supplies. The facility must:

(a) Keep the buildings in a clean, safe and orderly condition. This includes all rooms, corridors, attics, basements and storage areas.

(b) Keep floors clean and as non-slip as practicable to ensure resident safety.

(c) Control odors within the housekeeping staff's areas of responsibility by effective cleaning procedures and by the proper use of ventilation. Deodorants must not be used to cover up odors caused by unsanitary conditions or poor housekeeping practices.

(d) Keep attics, basements, stairways and similar areas free of accumulations of refuse, discarded furniture, discarded equipment, newspapers, magazines, boxes and other similar items.

(e) Not use bathrooms, shower stalls and lavatories for laundering, janitorial or storage purposes.

(f) Store all cleaning compounds, insecticides and all other potentially hazardous compounds or agents in locked cabinets or rooms.

(4) The facility must have an effective written plan and must supply an adequate amount of clean linen based on the weather and climate for each resident. Linens must be in good condition to provide proper care and comfort to each resident, either through on-site laundry service or a contract with an outside service.

(a) The onsite laundry room must be maintained and operated in a clean, safe and sanitary manner.

(b) Written operating procedures must be developed, and implemented to provide for the handling and storage of clean and soiled linens. These operating procedures must be available upon request by facility staff or Agency representatives.

(c) Laundry personnel must be in good health and practice good personal hygiene and grooming. Employees must thoroughly wash their hands and exposed portions of their arms with soap and water before starting work, after smoking, eating, using the toilet or handling soiled linens.

(d) Clean linen must be protected from contamination during handling and storage.

(e) Soiled linen must be handled and stored in a manner that protects facility residents and personnel.

(f) If an outside laundry service is used, it must be in compliance with state and local health and environmental laws and must provide for protection of clean linens during transport back to the facility.

(g) Laundry services for residents' personal clothing, must be handled and clothing stored in a manner that will not allow contamination of clean linen by soiled linen. The licensee must ensure that the personal clothing of each resident is returned to that individual resident after laundering.

Specific Authority 400.967 FS. Law Implemented 400.967(2)(c) FS. History–New________.

59A-26.019 Fire Protection, Life Safety, Systems Failure, and External Emergency Communications.

(1) Standards for fire prevention for the facility are those set forth in Chapter 69A-38, F.A.C., Uniform Fire Safety Standards for Residential Facilities for Individuals with Developmental Disabilities, as applicable to the classifications of occupancy therein.

(2) The Agency must conduct an annual fire safety survey. Based upon the survey, a report of deficiencies will be provided to the facility with a specified time frame for correction.

(3) ICF/DDs providing personal care, as defined in the Life Safety Code NFPA 101 2003 edition, but not nursing care will be reviewed as Residential Board and Care occupancy status under chapter 32 or 33 of the Life Safety Code NFPA 101, 2003 edition. ICF/DDs providing nursing care will be reviewed as Health Care Facility occupancy status under chapters 18 or 19 of the Life Safety Code NFPA 101, 2003 edition. To assure the life safety code requirements are appropriate for all residents served in an ICF/DD, each licensure survey conducted after Apri1 1, 2006 shall establish or confirm the occupancy status. Beginning July 1, 2006, upon renewal of each ICF/DD license, the license shall display the occupancy status. The ICF/DD licensee must receive approval from the Agency, including the Office of Plans and Construction, prior to a change in the occupancy status. A resident requiring nursing care may not reside in an ICF/DD with a Residential Board and Care occupancy status.

(4) Each licensee must provide fire protection through the elimination of fire hazards. All portions of the facility must comply with the requirements of the National Fire Protection Association (NFPA) Life Safety Code 101, as adopted by the State Fire Marshal and described in Chapter 69A-38 F.A.C., and incorporated by reference and obtainable from the National Fire Protection Association, 1 Batterymarch Park, P.O. Box 9101, Quincy, Massachusetts 02269-9101.

(5) All fires or explosions must be reported by the licensee within 24 hours by phone to the Agency for Health Care Administration’s field office, and the Office of Plans and Construction. Upon notification and in accordance with NFPA 1, Fire Prevention Code, the Office of Plans and Construction must investigate the cause, origin, and circumstances of the fire or explosion. To facilitate this investigation, the licensee must complete the form “Fire Incident Report, AHCA #3500-0031, May 1998”, revised 2000, incorporated herein by reference and available from the Office of Plans and Construction, Agency for Health Care Administration, 2727 Mahan Drive, Mail Stop 24 Tallahassee, Florida, 32308 or from the web site at www.ahca.myflorida.com. The form must be completed by the licensee and submitted to the Agency’s Office of Plans and Construction within 10 calendar days of the incident.

(6) In accordance with NFPA 101, Life Safety Code, in the event of a system failure of the fire alarm system, smoke detection system, or sprinkler system, the following actions must be taken immediately by the licensee:

(a) Notify the local fire authority and document instructions.

(b) Notify the Agency for Health Care Administration Office of Plans and Construction, and the Agency’s local field office:

(c) Assess the extent of the condition and effect corrective action, with a documented period for compliance. If the corrective action will take more than four (4) hours, the following items must be completed:

1. Implement a contingency plan containing a description of the problem, a specific description of the system failure, and the projected correction period. All staff on shifts involved must have documented in-service training for the emergency contingency.

2. Begin a documented fire watch, until the system is restored. Persons used for fire watch must be trained in what to look for, what to do, and be able to expeditiously contact the fire department. To maintain a fire watch, the facility must utilize only certified public fire safety personnel, a guard service, or facility staff. If facility staff are utilized for this function, they must meet the following requirements:

a. Be off duty from their regular facility position or assigned only to fire watch duty and be excluded from counting toward the required staffing pattern.

b. Be trained and competent as determined by the licensee in the duties and responsibilities of a fire watch and;

c. Have immediate access to electronic communication.

3. If the projected correction period changes or when the system is restored to normal operation, the licensee must notify the Agency for Health Care Administration Office of Plans and Construction, the Agency’s local field office, and local fire authorities.

(7) External emergency communication. Each new facility must provide for external electronic communication not dependent on terrestrial telephone lines, cellular, radio or microwave towers, such as an on-site radio transmitter, satellite communication systems or a written agreement with an amateur radio operator volunteer group(s). If the latter, this agreement must provide for a volunteer operator and communication equipment to be relocated into the facility in the event of a disaster until communications are restored. Other methods, which can be shown to maintain uninterrupted electronic communications not dependent on land-based transmission, must be pre-approved by the Agency’s Office of Plans and Construction.

Specific Authority 400.967 FS. Law Implemented 400.967(2)(a) FS. History–New________.

59A-26.020 Plans Submission and Fee Requirements.

(1) All construction work, including demolition, must receive prior written approval from the Agency for Health Care Administration Office of Plans and Construction before any work can begin. This includes all construction of new facilities and any and all additions, modifications, alternations, renovations, and refurbishing to the site, facility, equipment or systems of any facility.

(2) Approval to start construction only for demolition, site work, foundation, and building structural frame may be obtained prior to construction document approval when the following is submitted for review and has been approved by the Agency’s Office of Plans and Construction:

(a) Preliminary Stage II approval letter from the Office of Plans and Construction.

(b) Construction documents, specifications and construction details for all work to be undertaken.

(c) A letter from the facility holding the Agency harmless for any changes that may occur to the project as a result of the final construction document review.

(d) A life safety plan indicating temporary egress and detailed phasing plans indicating how the area(s) to be demolished or constructed is to be separated from all occupied areas must be submitted for review and approval when demolition or construction in and around occupied buildings is to be undertaken.

(3) Projects that have been submitted for Agency Office of Plans and Construction review will be considered abandoned and will be disapproved after any of the following has occurred:

(a) Construction has not begun within one year after written approval of the construction documents from the Agency’s Office of Plans and Construction;

(b) No further plans have been submitted for Agency review within one year after a project has been initiated with the Office of Plans and Construction or;

(c) Construction has been halted for more than one year. After this termination, resubmission as a new project will be required.

(4) All plans and specifications provided to the Agency as required in this section must be prepared and submitted by a Florida-registered architect and a Florida-registered professional engineer. An architectural or engineering firm not practicing as a sole proprietor may prepare and submit plans and specifications to the Agency if they are registered as an architectural or engineering firm with the Florida Department of Business and Professional Regulation.

(5) The initial submission of plans to the Agency’s Office of Plans and Construction for any new project must include a completed Plan Review Application Form, ACHA Form 3500-0011 Nov. 96 revised March 02, incorporated by reference and obtainable from the Agency for Health Care Administration, 2727 Mahan Drive Mail Stop 24, Tallahassee, Florida, 32308 and a valid certificate of need, pursuant to Chapter 408 F.S., if required by the Agency. This information must accompany the initial submission. Approval will not be granted for any project without a certificate of need, pursuant to Chapter 408, F.S., if required by the Agency.

(6) Plans and specifications submitted for review shall be subject to a plan review fee. This fee is prescribed by s. 400.967 (6), F.S. All fees must be paid by check made payable to the Agency for Health Care Administration, with the check noted with the Office of Plans and Construction facility log number and identified that it is for the Agency’s Health Care Trust Fund. Fees will be accepted only from the ICF/DD licensee or prospective licensee.

(7) Plans and specifications must be submitted in three stages. Exceptions to the submission of all three stages shall be subject to prior approval by the Agency’s Office of Plans and Construction.

(a) Stage I, schematic plans.

(b) Stage II, preliminary plans or design development drawings.

(c) Stage III, construction documents, including specifications, addenda and change orders.

(8) For each stage of submission, a program or scope of work must be submitted. It must consist of a detailed word description of all contemplated work and any required phasing to be provided in the proposed construction.

(9) For projects involving only equipment changes or system renovations, only Stage III, construction documents need be submitted. These documents must include the following:

(a) Life safety plans showing the fire/smoke compartments in the area of renovation.

(b) Detailed phasing plans indicating how the new work will be separated from all occupied areas.

(c) Engineering plans and specifications for all of the required work.

(10) Stage I, schematic plans.

(a) At a minimum, the following must be incorporated into the schematic plans:

1. Single-line drawings of each floor showing the relationship of the various activities or services to each other and the room arrangement in each.

a. The function of each room or space must be noted in or near the room or space.

b. The proposed roads and walkways, service and entrance courts, parking, and orientation must be shown on either a small plot plan or on the first floor plan.

c. Provide a simple cross-section diagram showing the anticipated construction.

d. Provide a schematic life safety plan showing smoke and fire compartments, exits, and gross areas of smoke and fire compartments.

e. Provide information as to which areas are sprinkled, both proposed and existing.

2. If the proposed construction is an addition or is otherwise related to existing buildings on the site, the schematic plans must show the facility and general arrangement of those other buildings.

3. Provide a schedule showing the total number of beds, types of bedrooms and types of ancillary spaces.

(11) Stage II, preliminary plans.

(a) At a minimum, to gain a Stage II approval, the following must be incorporated into the preliminary plans:

1. Vicinity map. For new facility construction, provide a vicinity map showing the major local highway intersections.

2. Site development plans including:

a. Existing grades and proposed improvements as required by the schematic submission.

b. Building locating dimensions.

c. Site elevations for both the 100-year flood elevations and hurricane category 3 surge inundation elevations if the project involves the construction of a new facility or is a new addition of a wing or floor to a facility.

d. The location of the fire protection services water source to the building.

3. Architectural plans including:

a. Floor plans, 1/8-inch scale minimum, showing door swings, windows, casework and millwork, fixed equipment and plumbing fixtures. Indicate the function of each space.

b. A large-scale plan of typical new bedrooms with a tabulation of gross and net square footage of each bedroom. Tabulate the size of the bedroom window glass.

c. Typical large-scale interior and exterior wall sections to include typical rated fire and fire/smoke partitions and a typical corridor partition.

d. All exterior building elevations.

e. Identification of equipment, which is not included in the construction contract but which requires mechanical or electrical service connections or construction modifications, to assure its coordination with the architectural, mechanical and electrical phases of construction.

f. Preliminary phasing plans indicating how the project is to be separated from all occupied areas must be provided if the project is located in an occupied facility.

4. Life safety plans including:

a. Single-sheet floor plans showing fire and smoke compartmentation, all means of egress and all exit signs. The dimension of the longest path of travel in each smoke compartment to the door(s) to the adjoining compartment, the total area of the smoke compartment in square feet, and tabulated exit in inches must also be provided.

b. All sprinkled areas, fire extinguishers, fire alarm devices and pull station locations.

c. Fully developed life safety plans must be submitted if the project is an addition or conversion of an existing building.

d. Life safety plans of the floor being renovated and the required exit egress floor(s) if the project is a renovation in an existing building.

e. A life safety plan indicating temporary egress and detailed phasing plans indicating how the area(s) to be demolished or constructed are to be separated from all occupied areas when demolition or construction in and around occupied buildings is to be undertaken.

5. Mechanical engineering plans including:

a. Single-sheet floor plans with a one-line diagram of the ventilating system with relative pressures of each space.

b. A written description and drawings of the anticipated smoke control system, passive or active, and a sequence of operation correlated with the life safety plans.

c. The general location of all fire and smoke dampers, all duct smoke detectors and firestats.

d. The location of the sprinkler system risers and the point of connection for the fire sprinkler system if the building is equipped with fire sprinklers, including the method of design for the existing and new fire sprinkler systems.

e. Locations of all plumbing fixtures and other items of equipment requiring plumbing services and/or gas services.

f. Locations of all medical gas outlets, piping distribution risers, terminals, alarm panel(s), low pressure emergency oxygen connection, isolation/zone valve(s), and gas source location(s).

g. Locations and relative sizes of major items of mechanical equipment such as chillers, air handling units, fire pumps, medical gas storage, boilers, vacuum pumps, air compressors, large storage batteries, and fuel storage vessels.

h. Locations of hazardous areas and the volume of products to be contained therein.

i. Location of fire pump, stand pipes, and sprinkler riser(s).

6. Electrical engineering drawings including:

a. A one-line diagram of normal and essential electrical power systems showing service transformers and entrances, switchboards, transfer switches, distribution feeders and over-current devices, panel boards and step-down transformers. The diagram must include a preliminary listing and description of new and existing, normal and emergency loads, preliminary estimates of available short-circuit current at all new equipment and existing equipment serving any new equipment, short-circuit and withstand ratings of existing equipment serving new loads and any new or revised grounding requirements.

b. Fire alarm zones correlated with the life safety plan.

7. Outline specifications. Outline specifications are to include a general description of the construction, including construction classification and ratings of components, interior finishes, general types and locations of acoustical material, floor coverings, electrical equipment, ventilating equipment and plumbing fixtures, fire protection equipment, and medical gas equipment.

8. Whenever an existing structure is to be converted to an ICF/DD facility, the general layout of spaces of the existing structure must be submitted with the preliminary plans for the proposed facility.

9. Whenever additions, modifications, alterations, renovations, and refurbishing to a facility are proposed, the general layout of spaces of the facility must be submitted with the preliminary plans.

(12) Stage III, construction documents.

(a) The Stage III, construction documents must be an extension of the Stage II, preliminary plan submission and must provide a complete description of the contemplated construction. Construction documents must be signed, sealed, dated and submitted for written approval to the Agency’s Office of Plans and Construction by a Florida-registered architect and Florida-registered professional engineer. These documents must consist of work related to civil, structural, mechanical, and electrical engineering, fire protection, lightning protection, landscape architecture and all architectural work. At a minimum, and in addition to the requirements for Stage II submission, the following must be incorporated into the construction documents:

1. Provide site and civil engineering plans that must indicate building and site elevations, site utilities, paving plans, grading and drainage plans and details, locations of the two fire hydrants utilized to perform the water supply flow test, and landscaping plans.

2. Provide life safety plans for the entire project.

3. Provide architectural plans, including:

a. Typical large-scale details of all typical interior and exterior walls and smoke walls, horizontal exits and exit passageways.

b. Comprehensive ceiling plans that show all utilities, lighting fixtures, smoke detectors, ventilation devices, sprinkler head locations and fire-rated ceiling suspension member locations where applicable.

c. Floor/ceiling and roof/ceiling assembly descriptions for all conditions.

d. Details and other instructions to the contractor on the construction documents describing the techniques to be used to seal floor construction penetrations to the extent necessary to prevent smoke migration from floor to floor during a fire.

4. Structural engineering plans, schedules and details.

5. Mechanical engineering plans to include fire and smoke control plans, including:

a. All items of owner furnished equipment requiring mechanical services.

b. A clear and concise narrative control sequence of operations for each item of mechanical equipment including but not limited to air conditioning, heating, ventilation, medical gas, plumbing, and fire protection and any interconnection of the equipment of the systems.

c. Mechanical engineering drawings that depict completely the systems to be utilized, whether new or existing, from the point of system origination to its termination.

d. A tabular schedule giving the required air flow (as computed from the information contained on the ventilation rate table) in cubic feet per minute (cfm) for supply, return, exhaust, outdoor, and ventilation air for each space listed or referenced by note on the ventilation rate table as shown on the architectural documents. The schedule must also contain the Heating Ventilation and Air Conditioning (HVAC) system design air flow rates and the resulting space relative pressures.

e. The schedule or portion of the schedule, as applicable, which must be placed in the specifications or in the drawing set containing the spaces depicted.

6. Fire protection plans, where applicable, that must include the existing system as necessary to define the new work.

7. Electrical engineering plans that must describe complete power, lighting, alarm, communications and lightning protection systems and power system study.

8. A power study that must include a fault study complete with calculations to demonstrate that over-current devices, transfer switches, switchboards, panel boards, motor controls, transformers and feeders are adequately sized to safely withstand available phase-to-phase and phase-to-ground faults. The study must also include an analysis of generator performance under fault conditions and a coordination study resulting in the tabulation of settings for all over-current device adjustable trips, time delays, relays and ground fault coordination. This must be provided for all new equipment and existing equipment serving any new equipment. Power studies for renovations of existing distribution systems must include only new equipment and existing equipment upstream to the normal and emergency sources of the new equipment. Renovations involving only branch circuit panel boards without modifications to the feeder must not require a full power study; instead, the power study must be limited to the calculation of new and existing loads of the branch circuit panel.

9. A complete set of specifications for all work to be undertaken.

a. All project required contractor supplied testing and/or certification reports must be typed on standard forms, reviewed and accepted by the engineer of record prior to presenting to the Agency’s Office of Plans and Construction for review.

b. The specifications must require a performance verification test and balance air quantity values report for a minimum of two operating conditions for each air handling unit system. One operating condition must be with the specified air filters installed in the minimum pressure drop or clean state. The second operating condition is to be at the maximum pressure drop and/or dirty state. The air quantities reported are acceptable if they are within 10 percent of the design value and the space relative pressures are maintained. This requirement must apply to any air-handling unit affected by the construction to be performed.

10. All construction documents must be well coordinated. It is specifically required that in the case of additions to facilities, the mechanical and electrical, especially existing essential electrical systems and all other pertinent conditions, must be a part of this submission.

11. All subsequent addenda, change orders, field orders and other documents altering the above must also be signed, sealed and dated and submitted in advance to the Agency’s Office of Plans and Construction for written approval.

(13) The initial submission will be acted upon by the Agency Office of Plans and Construction within 60 days of the receipt of the initial payment of the plan review fee. The Agency will either approve or disapprove the submission and shall provide a listing of deficiencies in writing. Each subsequent resubmission of documents for review on the project will initiate another 60-day response period. If the Agency does not act within 60 days of receipt of a submission, the submission will be considered approved. However, all deficiencies noted by the Agency must still be satisfactorily corrected before final approval may be obtained for the project.

(14) Additions or revisions that substantially change the original scope of the project or are submitted by different design professionals, will be required to be submitted as a new project.

Specific Authority 400.967 FS. Law Implemented 400.967(2), (5), (6) FS. History–New________.

59A-26.021 Physical Plant Codes and Standards for ICF/DD.

(1) After April 1, 2006 all construction of new facilities or conversions and all additions, modifications, alterations, renovations, and refurbishing to the site, facility, equipment or systems of a facility must be in compliance with the following codes and standards:

(a) The Florida Building Code, as adopted by the Florida Building Commission and incorporated by reference in Rule 9B-3.047, F.A.C., by the Department of Community Affairs and obtainable from the Southern Building Code Congress International, Inc., 900 Montclair Road, Birmingham, Alabama 35213-1206.

(b) The fire codes as adopted by the State Fire Marshal and incorporated by reference in Rule 69A-38 F.A.C., by the Division of State Fire Marshal at the Department of Finance and obtainable from the National Fire Protection Association, 1 Batterymarch Park, P.O. Box 9101, Quincy, Massachusetts 02269-9101.

(c) When the level of care of the residents of the facility is classified as level 7, 8 or 9, or if a facility is providing skilled/acute nursing or medical care such as is provided in a hospital, nursing home or an inpatient hospice, NFPA 101, Chapter 18 or 19, (Health Care Occupancies) must be applied.

(2) The Fire Safety Evaluation System (FSES) NFPA-101 A as adopted by the State Fire Marshal and described in Chapter 69A-3.012 F.A.C., and herein incorporated by reference and obtainable from the National Fire Protection Association, 1 Batterymarch Park, P.O. Box 9101, Quincy, Massachusetts 02269-9101, must not be used to meet the required codes and standards for new construction, renovations, or for conversion of an existing building to a new licensed ICF/DD.

(3) Where additions, modifications, alterations, refurbishing, renovations or reconstruction are undertaken within a facility, all such additions, modifications, alterations, refurbishing, renovations or reconstruction must comply with applicable sections of the codes for new facilities. Where major structural elements make total compliance impractical or impossible, the licensee or potential licensee must submit to the Agency’s Office of Plans and Construction a request to utilize alternate materials and methods in accordance with the Florida Building Code.

(4) At a minimum all existing facilities not classified as Health Care Occupancy must be in compliance with the requirements of Chapter 33, Existing Residential Board and Care Occupancy, of the National Fire Protection Association (NFPA) Life Safety Code 101, as adopted by the State Fire Marshal and described in Chapter 69A-38 F.A.C., and with Chapter 34, Existing Buildings of the Florida Building Code, 2003 edition.

Specific Authority 400.967 FS. Law Implemented 400.967(2)(a) FS. History–New________.

59A-26.022 Construction and Physical Environment Standards.

After April 1, 2006 all new facilities must be in compliance with the following minimum physical plant standards:

(1) Site requirements.

(a) Each facility must be located on a site in compliance with local zoning codes, Chapter 400 Part XI, this rule, and if applicable, Chapter 419, F.S. The terrain must be such that effective drainage can be accomplished. Utilities must be commensurate with the facility's regular operational needs and emergencies. The site must be remote from uncontrolled or uncontrollable sources of insect and rodent harborage and air and water pollution.

(b) A site may include structures other than the ICF/DD facility such as storage sheds and greenhouses. Ancillary spaces may be available within the living units or in a separate on-site structure to provide services that cannot be purchased in the community or when residents are physically unable to attend community or therapy services.

(c) All new facilities or an addition of a wing or floor to a facility must be in compliance with the site requirements of this rule.

(2) Living unit requirements:

(a) Each living unit must provide for all residential functions and environmental characteristics with a home-like atmosphere.

(b) Residents must have a choice of a variety of comfortable living spaces.

(c) There must be sufficient equipment and appliances to meet the programmatic needs of all residents.

(d) Each living unit must have a kitchen that is adequate for preparing all meals, cleaning and storing of food and equipment. The kitchen design, appliances, equipment, materials and finishes must convey the image of a home-like kitchen.

(e) Each living unit must have a dining area.

(f) Provisions must be made to ensure meals are eaten at the dining table with appropriate positioning devices, chairs or wheelchairs for each resident as needed.

(g) Sufficient space must be provided to accommodate resident needs for indoor gross motor, fine motor and special teaching activities within the facility.

(h) Each resident living unit must have 3 or more bedrooms.

1. Each resident must have accessible personal space within the bedroom to accommodate an individual bed and personal furnishings, and to decorate and arrange without disturbing others. This space must also be utilized to store personal possessions.

2. Each bedroom must have a minimum of 100 square feet (9.29 square meters) of clear floor area per bed in multiple-bed rooms and 120 square feet (11.15 square meters) of clear floor area in single-bed rooms, exclusive of the space consumed by toilet rooms, closets, lockers, wardrobes, lavatories, alcoves, entrance vestibules, and the area taken up by all door swings that open into the room. For the purpose of minimum clear floor area, the entrance vestibule is defined as that floor area located between the room entrance door and the room floor area containing any resident bed. The dimensions and arrangement of rooms must provide a minimum of 3 feet (0.91 meter) between the sides and foot of the bed and any wall or any other fixed obstruction or adjacent bed. In multiple-bed rooms, a clearance of 3 feet 8 inches (1.11 meters) to any fixed obstruction must be available at the foot of each bed to permit the passage of equipment and beds. Where renovation work is undertaken, every effort must be made to meet these minimum space standards. When this is not possible due to existing physical constraints, and with the prior approval of the Agency’s Office of Plans and Construction, resident rooms must have no less than 80 square feet (7.43 square meters) of clear floor area per bed in multiple-bed rooms and 100 square feet (9.29 square meters) of clear floor area in single-bed rooms exclusive of toilet rooms, closets, lockers, wardrobes, lavatories, alcoves and entrance vestibules. This requirement does not limit the licensee’s prerogative to exceed minimum standards in this respect, and the accessible area provided must accommodate the needs of the residents occupying the space. The maximum number of residents sharing a bedroom shall be 2.

(i)Corridors must be not less than 6 feet in clear and unobstructed width.

(j) Doors must not be less than 48 inches in clear width for means of egress from sleeping rooms.

(k) Each living unit must provide adequate space for all residents to carry out normal bathroom functions, or for assistance in carrying out these functions, including bathing, toileting, washing and grooming. Facilities must be as comparable to normal home-like standards as is appropriate to the functional level of residents. The standard range of bathroom fixtures must be provided in adequate numbers and in standard residential arrangements providing privacy for residents in performing each function. Each resident must have access to a toilet room without having to enter the general corridor area. One toilet room shall serve no more than 4 beds and no more than 2 resident rooms. The toilet room door must be side-hinged, swing out from the toilet room, and unless otherwise required by the code, be at least 32 inches (81.28 centimeters) wide.

(l) Each living unit must provide a minimum of one multi-purpose staff workroom of not less than 120 square feet.

(m) Each living unit must be equipped to wash and dry the personal clothing of all residents residing in the living unit.

(n) Each living unit must provide outdoor activity spaces providing a variety of activities that are accessible to residents, and provide cover and protection from the elements.

(o) Each living unit must meet the requirements of Florida Building Code Chapter 11-6.1(2) for accessibility percentage of total accessible rooms.

(3) Details and finishes.

(a) Potential hazards such as sharp corners, or loose laid rugs or carpets, shall not be permitted.

(b) Doors to all rooms containing bathtubs, showers, and water closets for resident use must be equipped with privacy hardware that permits emergency access without keys. When such rooms have only one entrance or are small, the doors must open outward and, if on the corridor, must open into an alcove.

(c) All interior doors, except those that automatically close upon smoke detection, must be side-hinged swinging type. Interior corridor doors, except those to small closets not subject to occupancy, shall not swing into the corridor.

(d) Operable windows must be equipped with insect screens.

(e) Threshold covers must be designed to facilitate use of wheelchairs and carts and to prevent tripping and shall provide a smooth and level transition from surface to surface.

(f) Grab bars, 1-1/2 inches (3.8 centimeters) in diameter, must be installed in all resident showers, tubs, and baths and on both sides of all resident use toilets. Wall-mounted grab bars shall provide a 1-1/2 inch (3.8 centimeters) clearance from walls and shall sustain a concentrated load of 250 pounds (113.4 kilograms).

(g) Handrails with a maximum diameter of 1-1/2 inches (3.8 centimeters) must be provided on both sides of all corridors normally used by residents. Mounting height shall be between 36 inches (91.4 centimeters) and 42 inches (106.7 centimeters). A clearance of 1-1/2 inches (3.8 centimeters) must be provided between the handrail and the wall. Rail ends shall return to the wall.

(h) Each resident hand washing facility must have a mirror for the resident unless prohibited by the interdisciplinary team. Mirror placement must allow for convenient use by both wheelchair occupants and ambulatory persons. Tops and bottoms may be at levels usable by residents either sitting or standing. Additional mirrors may be provided for wheelchair residents, or one separate full-length mirror located in the resident room may be provided to meet the needs of wheelchair residents. All mirrors must provide a distortion free image.

(i) Provisions for soap dispensing and hand drying must be included at all hand washing facilities. Hand drying provisions in resident use areas shall be paper or cloth towels enclosed to protect against dust or soil and shall be single-unit dispensing.

(j) The minimum ceiling height in occupiable rooms and habitable spaces throughout the facility must be 8 feet 0 inches (2.44 meters) above the finished floor. Ceilings in corridors, resident room entrance, vestibules and toilet rooms must be a minimum of 7 feet 6 inches (2.33 meters) above the finished floor.

(k) Only recessed soap dishes may be allowed in patient use tubs and showers. Towel bars must be provided at each bathing area.

(l) A minimum of one electric drinking fountain must be provided per facility living unit as required by the Florida Plumbing Code.

(m) Floor material must be readily cleanable and appropriate for the location. If composition floor tiles are used, the interstices must be tight. In residential care and sleeping areas, a base must be provided at the floor line. Floors in areas used for food preparation and assembly must be water-resistant. Floor surfaces, including tile joints, must be resistant to food acids. In all areas subject to frequent wet-cleaning methods, floor materials must not be physically affected by germicidal cleaning solutions. Floors subject to traffic while wet, such as shower and bath areas, kitchens, and similar work areas, must have a slip resistant surface and floor-to-base intersections must be watertight. Carpet and padding in resident areas must be stretched tight, in good repair and free of loose edges or wrinkles that might create hazards or interfere with the operation of wheelchairs, walkers, or wheeled carts.

(n) Wall finishes must be washable and, if near plumbing fixtures, must be smooth and have a moisture-resistant finish. Finish, trim, walls, and floor constructions in dietary and food storage areas must be free from rodent and insect harboring spaces.

(o) Basic wall construction in areas not subject to conditioned air must be constructed of masonry, cement, plaster or moisture resistant gypsum wallboard.

(p) The finishes of all exposed ceilings and ceiling structures in the dietary facilities area must be readily cleanable with routine housekeeping equipment.

(q) All smoke partitions must be constructed prior to the construction of intervening walls.

(r) Smoke partitions must be constructed so as to provide a continuous smoke-tight membrane from exterior wall to exterior wall and from the floor to the underside of the deck above. This includes interstitial space and the area above solid fire-tested membranes. Where it is not possible to inspect smoke partitions because of the fire-tested membrane, fire-rated access panels must be installed adjacent to each side of the smoke partitions at intervals not exceeding 30 feet (9.00 meters) and in such locations as necessary to view all surfaces of the partition.

Where electrical conduits, cable trays, ducts and utility pipes pass through the smoke partition, the utilities must be located so that access is maintained to adjacent wall surfaces and to all damper access panels. The details must show the studs and reinforcing half studs so that proper support is provided for the wall surfacing material. There must be a minimum clearance of 6 inches (15.29 centimeters) between all conduits, piping, and ductwork at corridor walls to facilitate the inspection of these walls.

(4) Mechanical system requirements:

(a) Mechanical equipment shall be defined as equipment utilized in air conditioning, heating, ventilating systems and associated electrical, electronic and pneumatic components required for the mechanical equipment to provide the function intended by the application of the equipment. New and existing equipment replacements must comply with these requirements.

(b) Mechanical equipment must be installed in a designated equipment room(s), or in a space(s) located in an attic(s). If the unit serves only one room it may be located above the ceiling and must be accessible through an access opening in accordance with the Florida Building Code. Access panels are not required for lay-in ceiling installations provided the service functions are not obstructed by other above-ceiling construction such as electrical conduits, piping, audio visual cabling and like equipment components or supports.

(c) Ventilation must be provided by mechanical means in all rooms in new facilities and in all renovated or remodeled rooms of a facility. The minimum air quantities and filtration efficiencies must be met as set forth in the Minimum Ventilation Rate Table for those spaces that are listed as required in the Florida Building Code, Chapter 4, Section 420.

(d) For spaces listed in the Minimum Ventilation Rate Table, central station type air handling equipment must be used. Package terminal air conditioning units or fan coils may be used to serve resident rooms and shall be provided with 20 percent filters minimum.

(e) System designs utilizing fan coil or package terminal air conditioning units must have the outdoor air ventilation damper permanently closed. The ventilation requirement must be satisfied by a central station type air handling unit provided with a 30 percent filter minimum or as required by the listed space served. Spaces designated for the exclusive use of physical plant personnel need not comply with this requirement.

MINIMUM VENTILATION RATE

| ROOM NAME OR AREA FUNCTION | SPACE RELATIVE PRESSURE NOTE 1 | TOTAL AIR QUANTITIES NOTE 2 | OUTDOOR AIR QUANTITIES NOTE 2 | EXHAUST 100 PERCENT | FILTRATION EFFICIENCY PERCENT NOTES 3&4 |
| --- | --- | --- | --- | --- | --- |
| Clean Linen, Utility or Holding | OUT | 4 | 2.00 | No | 30 |
| Dining | -- | 4 | 2.00 | No | 30 |
| Housekeeping/ Janitor’s Closet | IN | 10 | -- | Yes | 30 |
| Medicine Preparation Room | OUT | 4 | 2.00 | No | 80 |
| Nourishment Station | -- | 4 | 2.00 | No | 30 |
| Resident Corridor | -- | 2 | 1.00 | No | 30 |
| Resident Room (Note 4) | -- | 2 | 2.00 | No | 80 |
| Soiled Linen, Utility or Holding | IN | 10 | -- | Yes | 30 |
| Storage | -- | 2 | -- | No | 30 |
| Toilets and Baths | IN | 10 | -- | Yes | 30 |

Notes to Minimum Ventilation Rate Table: (1–5)

1. Design of the ventilation system shall provide air movement that is generally from clean to less clean areas. Air movement is in relationship to the adjacent room or area and is designated as OUT (or positive), IN (or negative) and -- (or neutral). If any form of variable-air-volume or load shedding system is used for energy conservation, it must not compromise the room pressure balancing relationships or the minimum air changes required by the table.

2. Tabular numerical values are space volume (cubic feet or cubic meters) per hour.

3. Filtration efficiency ratings are based on average dust spot efficiency per ASHRAE Standard 52.1-92.

4. Filter values apply to central station type air handling units. Where package terminal or fan coil air conditioning units are utilized, filter efficiency value may be 20 percent minimum.

5. Rooms or areas where specific ventilation rates are not given in the table must be ventilated in accordance with the American Society of Heating, Refrigerating, and Air Conditioning Engineers (ASHRAE) Standard 62, Ventilation for Acceptable Indoor Air Quality and ASHRAE Handbook-HVAC Applications. OSHA standards and NIOSH criteria require special ventilation requirements for employee health and safety within nursing facilities. For multi-function room designations, the most stringent tabular requirement shall govern.

(f) Administrative and other staff-only areas must be provided with outside air at the minimum rate of 20 cubic feet per minute (9.43 liters/second) per person, and the central system must have a minimum of 30 percent American Society of Heating Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE), 1995 Edition dust spot efficiency filter. Available from American Society of Heating Refrigerating and Air Conditioning Engineers, Inc. (ASHRAE), 1791 Tullie Circle NE, Atlanta, GA 30329.

(g) All filters in systems in excess of 1000 cubic feet per minute (28.32 cubic meters/minute) capacity must be installed with differential pressure gauges. The filter gauge must have the range of acceptable filter operation clearly and permanently indicated.

(h) Filter housings for 80 percent efficiency filters must be fully gasketed and sealed with mechanical latching devices capable of exerting and maintaining a continuous, uniform sealing pressure on the filter media when in the latched, closed position.

(i) The transfer of air quantities through one space to an adjacent space is not permitted except that the transfer of air to maintain space relative pressure by the under cutting of doors is permitted. The maximum allowable air quantity for door undercuts shall be 75 cubic feet per minute (35.38 liters per second) for single door widths up to 44 inches (111.7 centimeters).

(j)Space relative pressure requirements must be maintained throughout the entire system control range where variable volume systems are utilized.

(k)Spaces having exhaust hoods must have sufficient make-up supply air such that the required pressure relationship will not be affected by the operation of the hood.

(l) All supply, return and exhaust ventilation fans must operate continuously. Dietary hood, laundry area, administrative areas that are separated from all resident areas and support areas, and maintenance area supply and exhaust fans shall be exempted from continuous operation.

(m) Cooling coil condensate must be piped to a roof drain, floor drain or other approved location.

(n) Exhaust fans and other fans operating in conjunction with a negative duct system pressure must be located at the discharge end of the system. Fans located immediately within the building located at the end of all exhaust ducts shall be permitted. Existing, nonconforming systems need not be brought into compliance when equipment is replaced due to equipment failure.

(o) All new facility construction must have totally ducted supply, return, exhaust and outside air systems including areas of all occupancy classifications.

(p) During a fire alarm, fan systems and fan equipment serving more than one room must be stopped to prevent the movement of smoke by mechanical means from the zone in alarm to adjacent smoke zones.

(q) Air handling and fan coil units serving exit access corridors for the zone in alarm must shut down upon fire alarm.

(r) Smoke or fire/smoke dampers must close upon fire alarm and upon manual shutdown of the associated supply, return or exhaust fan.

(s) Mixing valves used in shower applications must be of the balanced-pressure type design.

(t)The temperature of hot water supplied to resident use lavatories, showers and bath must be between 105ºF. (45.5ºC) and 110ºF (46.1ºC) at the discharge end of the fixture.

(u) Wall mounted water closets, lavatories, drinking fountains and hand washing facilities must be attached to floor mounted carriers and shall withstand an applied vertical load of a minimum of 250 pounds (113.39 kilograms) to the front of the fixture and provide deep seal traps for floor drains in resident showers.

(v) Ice machines, rinse sinks, dishwashers, and beverage dispenser drip receptacles must be indirectly wasted.

(w) Each water service main, branch main, riser and branch to a group of fixtures must have valves. Stop valves must be provided for each fixture. Panels for valve access must be provided at all valves.

(x) Backflow preventers (vacuum breakers) must be installed on bedpan-rinsing attachments, hose bibs and supply nozzles used for connection of hoses or tubing in housekeeping sinks and similar applications.

(y) A backflow preventer must be installed on the facility main water source(s).

(5) Electrical requirements:

(a) All material, including equipment, conductors, controls, and signaling devices, must be installed to provide a complete electrical system with the necessary characteristics and capacity to supply the electrical facility requirements as shown in the specifications and as indicated on the plans. All materials and equipment must be listed as complying with applicable standards of Underwriter's Laboratories, Inc., or other nationally recognized testing facilities. Field labeling of equipment and materials will be permitted only when provided by a Nationally Recognized Testing Laboratory (NRTL) that has been certified by the Occupational Safety & Health Administration (OSHA) for that referenced standard.

(b) For purposes of this section, a resident room, a resident therapy area or an examination room shall be considered a "patient care area" as described in NFPA 99 "Health Care Facilities, and Chapter 27, "Electrical Systems" of the Florida Building Code.

(c) Panels located in spaces subject to storage must have the clear working space per Chapter 27, "Electrical Systems" of the Florida Building Code, permanently marked "Electrical Access - Not For Storage" with a line outlining the required clear working space on the floor and wall.

(d) Panels and electrical equipment, other than branch circuit devices serving the corridor, must not be located in egress corridors in new construction.

(e) Lighting.

1.All spaces occupied by people, machinery and equipment within buildings, approaches to buildings and parking lots must have electric lighting.

2. Resident bedrooms must have general lighting and separate fixed night lighting. The night-light must have a switch at the entrance to each resident's room. A reading light must be provided for each resident. Resident reading lights and other fixed lights not switched at the door must have switch controls convenient for use at the luminary. Wall-mounted switches for control of lighting in resident area must be of quiet operating type.

(f) Receptacles.

1. Provide one general purpose receptacle on another wall to serve each resident and one additional receptacle at the head of the bed if a motorized bed is provided.

2. Duplex receptacles for general use must be installed in all general purpose corridors, approximately 50 feet (15.24 meters) apart and within 25 feet (7.62 meters) of corridor ends.

(g) Fire alarm systems.

1. A fire alarm annunciator panel must be provided at a single designated 24-hour monitored location. The panel must indicate audibly & visually, the zone of actuation of the alarm and system trouble. As a minimum, devices located in each smoke compartment must be interconnected as a separate fire alarm zone. Annunciator wiring must be supervised. Annunciators must clearly indicate the zone location of the alarm. An adjacent zone location map to quickly locate alarm condition must be provided.

(h) Nurse call systems. Each facility must have a nurse call system that meets the following requirements.

1. A nurse call system must be provided that will register a call from each resident bed to the related staff work area(s) by activating a visual signal at the resident room door and activating a visual and audible signal in the clean utility, soiled utility, nourishment station, medication prep and the master station of the nursing unit or sub-nursing unit. Audible signals may be temporarily silenced provided subsequent calls automatically reactivate the audible signal. In rooms containing two or more calling stations indicating lights must be provided for each calling station. In multi-corridor nursing units corridor zone lights must be installed at corridor intersections in the vicinity of staff work areas.

2. An emergency calling station of the pull cord type must be provided and must be conveniently located for resident use at each resident toilet, bath or shower room but not inside the shower. The call signal must be the highest priority and shall be cancelled only at the emergency calling station. The emergency station must activate distinctive audible and visual signals immediately.

3. The nurse call master station must not block incoming resident calls. The master station control settings must not prevent the activation of the incoming audible and visual signals.

4. In multi-resident rooms, activation of an emergency call shall not cancel a normal call from the same room.

5. A corridor dome light must be located directly outside of any resident care area that is equipped with a nurse call station.

(i) Emergency electrical system.

1. A Type 1 essential electrical system must be provided in all ICF/DD facilities as described in NFPA 99, "Health Care Facilities" The emergency power for this system must meet the requirements of a Level 1, Type 10, Class 48 generator as described in NFPA 110, "Emergency Standby Power Systems".

2. In new construction, the normal main service equipment must be separated from the emergency distribution equipment by locating it in a separate room. Transfer switches must be considered emergency distribution equipment for this purpose.

3. Switches for critical branch lighting must be completely separate from normal switching. The devices or cover plates must be of a distinctive color. Critical branch switches may be adjacent to normal switches. Switches for life safety lighting are not permitted except as required for dusk-to-dawn automatic control of exterior lighting fixtures.

4. There must be selected life safety lighting provided at a minimum of 1 footcandle and designed for automatic dusk-to-dawn operation along the travel paths from the exits to the public way or to safe areas located a minimum of 30 feet (9.14 meters) from the building.

5. If a day tank is provided, it must be equipped with a dedicated low level fuel alarm and a manual pump. The alarm must be located at the generator derangement panel.

6. Transfer switch contacts must be of the open type and must be accessible for inspection and replacement.

7. If required by the facility's emergency food plan, there must be power connected to the equipment branch of the essential electrical system for kitchen refrigerators, freezers and range hood exhaust fans. Selected lighting within the kitchen and dry storage areas must be connected to the critical branch of the essential electrical system.

(6) Other general requirements.

(a) There must be at least one telephone, and it will be accessible to the residents.

(b) An accessible, adequate, safe, acceptable, and potable supply of water must be provided in all facilities and must be in compliance with Chapter 64E-8, F.A.C.

(c) An adequate and safe method of sewage collection, treatment and disposal must be provided in each facility and must be in compliance with Chapter 17-6, F.A.C., Sewage Works, or Chapter 64E-6, F.A.C., Individual Sewage Disposal. Whenever a municipal or public sewer system is available to the property, such system must be used. All plans regarding wastewater collection and treatment facilities must be approved by the Department of Environmental Regulation.

(d) In all facilities, vermin must be controlled in all areas of the facility in compliance with Chapter 64E-11, F.A.C., Insecticides and rodenticides must be handled in accordance with Chapter 5E-14.101-116, F.A.C.

(e) All facilities must comply with the requirements of 64E-16, F.A.C.

(7) Physical Plant Requirements for Disaster Resistance of ICF/DD Construction.

(a) Definitions. The following definitions must apply specifically to this section:

1. Existing Facility. A facility that prior to April 1, 2006;

a. Is licensed and certified, or

b. Has received a stage II preliminary plan approval from the Agency for a new facility.

2. New Facility. An ICF/DD licensed after April 1, 2006; or a facility that receives a Stage II Preliminary Plan approval after April 1, 2006; or an addition of a wing or floor to an existing ICF/DD, which has not received a Stage II Preliminary Plan approval pursuant to this section.

3. Net Square Footage. The clear floor space of an area excluding cabinetry and other fixed furniture or equipment.

4. During and Immediately Following. A period of 72 hours following the loss of normal support utilities to the facility.

5. Occupied Resident Area(s). The location of residents inside the new facility or in the addition of a wing or floor to an existing facility during and immediately following a disaster. If residents are to be relocated into an area of the existing facility during and immediately following a disaster, then for these purposes, that location will be defined as the “occupied resident area”.

6. Resident Support Area(s). The area(s) required to ensure the health, safety and well-being of residents during and immediately following a disaster, such as a staff work area, clean and soiled utility areas, food preparation area and other areas as determined by the licensee to be kept operational during and immediately following a disaster.

7. On-site - Either in, immediately adjacent to, or on the campus of the facility, or addition of a wing or floor to an existing facility.

8. Resident(s) Served. The number of residents as determined by the licensee that will be served in the occupied resident area(s) during and immediately following a disaster, including residents from other facilities, as applicable.

(b) New Facility Construction Standards. The following construction standards are in addition to the physical plant requirements described in this rule. These minimum standards are intended to increase the ability of the new facility to be structurally capable of serving as a shelter for residents, staff and the family of residents and staff and equipped to be self-supporting during and immediately following a disaster.

1. Space standards.

a. Each new facility must provide a minimum of 30 net square feet (2.79 square meters) per resident served in the occupied resident area(s). The number of residents served is to be determined by the facility.

b. Each licensee must have space for administrative and support activities and must be provided space for use by facility staff to allow for care of residents in the occupied resident area(s).

c. As determined by the licensee, space must be provided for all staff and family members of residents and staff.

2. Site standards.

a. All new facilities and additions to existing facilities must be located above the 100-year flood plain or hurricane Category 3 (Saffir-Simpson scale) hurricane surge inundation elevation as provided by the local county emergency management office, whichever requires the highest elevation, or

b. The floor elevation of all new occupied resident area(s) and all resident support area(s) and resident support utilities, including mechanical, electrical except fuel storage as noted in section 59A-26.022 (7)9.f., and food services must be located above the 100-year flood plain or hurricane Category 3 (Saffir-Simpson scale) hurricane surge inundation elevations whichever requires the highest elevation, or

c. New additions or floors added to existing facilities, as determined by their site locations, must be so designed and constructed as to be in compliance with the current standards of the National Flood Insurance Program of the Federal Emergency Management Agency, incorporated by reference and available from Federal Emergency Management Agency, Federal Insurance Administration, Attn. Publications, P.O. Box 70274, Washington, D.C. 20024.

d. Where an off-site public access route is available to the new facility at or above the 100-year flood plain, a minimum of one on-site emergency access route must be provided that is located at the same elevation as the public access route.

e. New landscaping elements must be located so if damaged they will not block the on-site emergency access route to the facility. Outdoor signs and their foundations must be designed to meet the wind load criteria of the Florida Building Code.

f. New light standards and their foundations used for lighting the on-site emergency access route must be designed to meet the wind load criteria of the American Society of Civil Engineers (ASCE 7-98), fifty-year recurrence interval of wind velocity with appropriate exposure category dependent on site location.

3. Structural standards. Wind load design of the building structure and exterior envelope including exterior wall systems must be designed in accordance with the Florida Building Code.

4. Roofing standards.

a. Roofing membrane material must resist the uplift forces specified in the Florida Building Code. Roof coverings must be installed according to the specifications provided by the manufacturer.

b. Loose-laid ballasted roofs are not permitted.

c. All new roof appendages such as ducts, tanks, ventilators, receivers, dx condensing units and decorative mansard roofs and their attachment systems must be structurally engineered to meet the wind load requirements of the Florida Building Code. All of these attachment systems must be connected directly to the underlying roof structure or roof support structure.

5. Exterior unit standards.

a. All exterior window units, skylights, exterior louvers and exterior door units including vision panels and their anchoring systems must be designed to resist the wind load requirements of the Florida Building Code and the debris impact requirements as specified by ss.1626.2-1626.4.

b. Permanently attached protective systems such as shutters and baffling must be designed to meet the wind load requirements of the Florida Building Code and the debris impact requirements as specified by ss.1626.2-1626.4.

c. Removable protective systems designed to fit intricately with the wall/window system of the facility, stored on-site at the facility, that meet the wind load requirements of the Florida Building Code and the debris impact requirements specified by ss.1626.2-1626.4 may be used to protect the exterior units.

d. All anchoring and attachments to the building of both the permanently attached and removable protective systems must be designed to meet wind load requirements of the Florida Building Code and the impact requirements specified by ss.1626.2-1626.4. These designs must be signed, sealed and dated by a Florida registered structural engineer.

e. The glazed openings inside or outside of the protective systems must meet the cyclical loading requirements specified by ss.1626.2-1626.4.

f. All of the exterior impact protective systems must be designed and installed so that they do not come in contact with the glazing under uniform, impact or cyclic pressure loading. The location or application of exterior impact protective systems must not prevent required exit/ egress from the building.

g. When not being used to protect the windows, the protective system must not restrict the operability (if provided) of the windows in the occupied resident bedrooms.

h. When not being used to protect the windows, the protective systems must not reduce the clear window opening below that required by the Florida Building Code for the resident room.

6. Heating, Ventilation and Air Conditioning (HVAC) Standards.

a. Air moving equipment, dx condensing units, through-wall units and other HVAC equipment located outside of or on the roof of the facility are permitted only when either of the following are met:

i. They are located inside a penthouse designed to meet the wind load requirements of the Florida Building Code, or

ii. Their fastening systems are designed to meet the wind load requirements of the Florida Building Code and they and all associated equipment are protected as specified in ss. 1626.2-1626.4 from damage by horizontal impact by a separate and independent structure that allows access to all parts of the equipment at all times.

b. All occupied resident areas and resident support areas must be supplied with sufficient HVAC as determined by the facility to ensure the health, safety and well being of all residents and staff during and immediately following a disaster.

c. As determined by the licensee these selected HVAC systems and their associated support equipment, such as a control air compressor essential to the maintenance of the occupied resident and resident support area(s), must receive their power from the emergency power supply system(s).

d. Ventilation air change rates in occupied resident areas must be maintained as specified in this section during and immediately following a disaster.

e. Auxiliary equipment and specialties such as hydronic supply piping and pneumatic control piping must be located, routed and protected in such a manner as determined by the licensee to ensure the equipment receiving the services will not be interrupted.

7. Plumbing standards.

a. There must be an independent on-site supply such as water well, or on-site storage capability such as empty water storage containers or bladders, of potable water at a minimum quantity of 3 gallons per resident served per day during and immediately following a disaster. Hot water in boilers or tanks must not be counted to meet this requirement.

b. There must be an independent on-site supply or storage capability of potable water at a minimum quantity of 1 gallon per facility staff, and other personnel in the facility per day during and immediately following a disaster. For planning purposes, the number of these personnel must be estimated by the licensee.

c. The licensee must determine what amount of water will be sufficient to provide for resident services, and must maintain an on-site supply or on-site storage of the determined amount.

d. When used to meet the minimum requirements of this rule, selected system appurtenances such as water pressure maintenance house pumps and emergency water supply well pumps must take power from the emergency power supply system.

8. Medical gas systems standards. The storage, distribution piping system and appurtenances must be contained within a protected area designed and constructed to meet the structural requirements of the Florida Building Code and debris impact requirements as specified by ss.1626.2-1626.4.

9. Emergency electrical generator and essential electrical system standards. There must be an on-site Level 1 emergency electrical generator system designed to support occupied resident areas and resident support areas with at least the following support services:

a. Ice making equipment to produce ice for the residents or freezer storage equipment for the storage of ice for the residents.

b. Refrigerator units and food service equipment as required by the emergency food plan.

c. At a minimum there must be one clothes washer and one clothes dryer for laundry service.

d. Selected HVAC systems as determined by the licensee and other systems required by the Florida Building Code.

e. An emergency generator system must be fueled by a fuel supply stored on-site sized to fuel the generator for 100 percent load for 64 hours or 72 hours for actual demand load of the occupied resident areas and resident support areas and resident support utilities during and immediately following a disaster, whichever is greater.

f. Fuel supply located below ground or contained within a protected area that is designed and constructed to meet the structural requirements of the Florida Building Code and debris impact requirements as specified by ss.1626.2-1626.4. If an underground system is used, it must be designed so as to exclude the entrance of any foreign solids or liquids.

g. Fuel lines supporting the generator system that are protected with a method designed and constructed to meet the structural requirements of the Florida Building Code and debris impact requirements as specified by ss.1626.2-1626.4.

h. Panel boards, transfer switches, disconnect switches, enclosed circuit breakers or emergency system raceway systems required to support the occupied resident area(s), resident support area(s) or support utilities which are contained within a protected area(s) designed and constructed to meet the structural requirements of the Florida Building Code and debris impact requirements as specified by ss.1626.2-1626.4, and that do not rely on systems or devices outside of this protected area(s) for their reliability or continuation of service.

i. An emergency generator(s) that is air-or self-contained- liquid cooled and which along with, other essential electrical equipment is installed in a protected area(s) designed and constructed to meet the structural requirements of the Florida Building Code and debris impact requirements as specified by ss.1626.2-1626.4.

j. If the facility does not have a permanent onsite optional standby generator to operate the normal branch electrical system, there shall be a permanently installed pre-designed electrical service entry for the normal branch electrical system that will allow a quick connection to a temporary electrical generator. This quick connection shall be installed inside of a permanent metal enclosure rated for this purpose and may be located on the exterior of the building.

10. Fire protection standards. If the facility requires fire sprinklers as part of its fire protection, one of the following must be met:

a. On-site water storage capacity to continue sprinkler coverage, in accordance with the requirements of NFPA 13, "Sprinkler Systems," fire watch, conducted in accordance with the requirements of NFPA 601.

b. If the facility provides a fire watch in lieu of water storage to continue sprinkler coverage, then one 4-A type fire extinguisher or equivalent must be provided for every 3 or less 2-A fire extinguishers required by NFPA 10, "Portable Extinguishers" for the area served. These additional extinguishers must be equally distributed throughout the area they are protecting.

11. External Emergency Communication. Each new facility must provide for an external electronic communication not dependent on terrestrial telephone lines, cellular, radio or microwave towers, such as on-site radio transmitter, satellite communication systems or a written agreement with an amateur radio operator volunteer group(s). This agreement must provide for a facility volunteer operator and communication equipment to be re-located into the facility in the event of a disaster until communications are restored. Other methods that can be shown to maintain uninterrupted electronic communications not dependent on land-based transmission must be pre-approved by the Agency’s Office of Plans and Construction.

Specific Authority 400.967 FS. Law Implemented 400.967(2)(a) FS. History–New________.

59A-26.023 Disaster Preparedness.

(1) Each licensee must have a written plan with procedures to be followed in the event of an internal or externally caused disaster or emergency event. The initiation, development, and maintenance of this plan must be the responsibility of the facility administrator, and must be reviewed and approved by the County Emergency Management Agency. The plan must be reviewed and approved annually and include, at a minimum, the following:

(a) Basic information concerning the facility to include:

1. Name of the facility, address, telephone number, 24 hour contact number if different from the facility number, emergency contact telephone number, and fax number.

2. Name of the licensee of the facility, address, telephone number.

3. Year facility was built, including type of construction.

4. Name of administrator, address, work and home telephone number.

5. Name, address, work and home telephone number of persons implementing the provisions of this plan, if different from the administrator.

6. An organizational chart showing all positions with key emergency positions identified by title, name and telephone numbers at home and work.

7. An organizational chart, if different from the previous chart required, identifying the hierarchy of authority in place during emergencies, and all positions on a day to day basis.

8. A description of the potential hazards that the facility is vulnerable to such as hurricanes, tornadoes, flooding, fires, hazardous materials incidents or transportation accidents, proximity to a nuclear power plant, power outages during severe cold or hot weather, including procedures for each of these hazards. Indicate past history and lessons learned.

9. Provide a copy of the Fire Safety Plan as stated in the Life Safety Code 2003 edition.

(b) Site specific information concerning the facility to include:

1. Number of facility beds and maximum number of residents on site.

2. Type of residents served by the facility to include, but not limited to, residents with seizure disorders, residents requiring special equipment such as wheelchairs, crutches, braces or other ambulatory assistance; residents with behavior or psychiatric disorders that may require one-to-one supervision; residents with special care needs such as oxygen, dialysis, or tube feeding.

3. Identification of the flood zone within which the facility is located as indicated on a Flood Insurance Rate Map.

4. Identification of the hurricane evacuation zone within which the facility is located.

5. Proximity of the facility to a railroad or major transportation artery (per hazardous materials incidents).

6. Whether the facility is located within the 10 or 50-mile emergency planning zone of a nuclear power plant. The 10 mile zone is called the Emergency Planning Zone (EPZ) and the 50 mile zone is called the Ingestion Pathway Zone (IPZ).

(c) Definition of management functions for emergency operations:

1. Identify by name and title, who is in charge during an emergency, and one alternate, should that person be unable to serve in that capacity.

2. Identify the chain of command to ensure continuous leadership and authority in key position.

3. Provide the procedures to ensure timely activation and staffing of the facility in emergency functions including any provisions for emergency workers' families.

4. Provide the operational and support roles for all facility staff. This may be accomplished through the development of standard operating procedures which must be attached to this plan.

5. Procedures to ensure the following are supplied:

a. Food, water and sleeping arrangements.

b. The type of emergency power, natural gas, diesel or other. If natural gas, identify alternate means should loss of power occur that would affect the natural gas system. Specify the capacity of the emergency fuel system.

c. Transportation of residents, staff and supplies.

d. Seventy-two hour supply of all essential supplies and resident medications.

e. 24-hour staffing on a continuing basis until the emergency has abated.

6. Procedures for the facility to receive timely information on impending threats and the alerting of facility decision makers, staff and residents to potential emergency conditions.

a. Define how the facility will receive warnings, to include, evenings, nights, weekends, and holidays.

b. Identify the facility 24-hour contact number, if different than the number listed in the introduction.

c. Define how key staff will be alerted.

d. Provide the procedures and policy for reporting to work for key workers.

e. Define how residents will be alerted and the precautionary measures that will be taken.

f. Identify primary notification and the alternative means of notification should the primary system fail for on duty and off duty staff.

g. Identify procedures for notifying the resident’s representative that the facility is being evacuated, including contact information for continued communication.

7. Provide the policies, responsibilities and procedures for the evacuation of residents from the facility.

a. Identify the individual responsible for implementing facility evacuation procedures.

b. Identify and provide transportation arrangements through mutual aid agreements that will be used to evacuate residents. These agreements must be in writing, and copies of these agreements must be submitted during plan review.

c. Describe transportation arrangements for logistical support to include moving records, medications, food, water, equipment and other necessities. Provide copies of agreements if transportation is provided by other than the licensee.

d. Identify the pre-determined locations to which residents will be evacuated.

e. Provide a copy of the mutual aid agreement that has been entered into with a facility to receive residents. It must include name, address, telephone number and contact person for the host facility. It must include the number of evacuees to be sheltered, including residents, staff and family members.

f. Provide evacuation routes, maps, written instructions and secondary routes that will be used should the primary route be impassable.

g. Specify the amount of time it will take to evacuate all residents successfully to the receiving facility.

h. Provide the procedures that ensure facility staff will accompany evacuating residents.

i. Provide the procedures to include a log system that will be used to keep track of residents once they have been evacuated.

j. Determine the items and supplies and the amount of each that should accompany each resident during the evacuation. Provide for a minimum 72-hour stay, with provisions to extend this period of time if needed.

k. Provide procedures for notifying resident representatives of evacuation.

l. Provide procedures for ensuring all residents are accounted for and are out of the facility.

m. Describe when the facility will begin the pre-positioning of necessary medical supplies and provisions.

n. Describe when and at what point the mutual aid agreements for transportation and the notification of alternative facilities will begin.

8. Provide the procedures that specify prerequisites needed and the process for residents to re-enter the facility.

a. Identify the responsible person for authorizing re-entry to occur.

b. Provide procedures for inspecting the facility to ensure it is structurally sound.

c. Identify how residents will be transported from the receiving facility back to their home facility and how the facility staff will receive accurate and timely data on re-entry operations.

9. If the facility is to be used as a receiving facility for an evacuating facility, describe the sheltering or hosting procedures that will be used once the evacuating residents arrive.

a. Describe the receiving procedures for residents arriving from the evacuating facility.

b. Identify where the additional residents will reside. Provide a floor plan, which identifies the room area where residents will be housed, room size, and number of residents per room or area.

c. Identify provision of additional food, water and medical needs of residents being hosted for a minimum of 72 hours.

d. Describe the procedures for ensuring 24-hour operations.

e. Describe procedures for providing shelter for family members of key workers.

f. Provide procedures for tracking additional residents sheltered within the facility.

10. Identify the procedures for increasing employee awareness of possible emergency situations and provide training on the emergency roles before, during and after an emergency, and on an annual basis.

a. Identify how key workers will be instructed in their emergency roles during non-emergency times.

b. Provide a training schedule for all employees and identify the providers of the training.

c. Identify the provisions for training new employees regarding their disaster related roles.

d. Provide the schedule for exercising all or portions of the emergency plan on an annual basis with all staff and all shifts.

11. If the licensee evacuates, the licensee must immediately, but within no more than 24 hours upon completion of evacuation, report to the Agency's Long Term Care Unit in Tallahassee at (850) 488-5861, the location and number of residents evacuated, and contact information for continued communication for the duration of the evacuation. In the event the Long Term Care Unit is unavailable to receive such information, contact the appropriate Agency field office.

Specific Authority 400.967(2) FS. Law Implemented 400.967(2)(g) FS. History–New________.