62-252.400 Gasoline Dispensing Facilities - Stage II Vapor Recovery.

(1) Applicability. The control technology requirements set forth in this section shall apply to all gasoline dispensing facilities located in Broward, Dade and Palm Beach counties which have dispensed 10,000 gallons (37,850 liters) or more of gasoline in any one month during or after 1991, unless the owner of any such facility demonstrates to the Department that it is an independent small business marketer of gasoline and has dispensed less than 50,000 gallons (189,250 liters) of gasoline in every month during and after 1991.

(2) Prohibition. No owner or operator of a gasoline dispensing facility subject to the provisions of this section shall transfer, allow the transfer, or provide equipment for the transfer of gasoline to a vehicular fuel tank unless the facility is equipped with a Stage II vapor recovery system which complies with the control technology requirements of subsection 62-252.400(3), F.A.C., and the system is properly used during the transfer.

(3) Control Technology Requirements.

(a) The Stage II vapor recovery system shall be 95 percent efficient in the recovery by weight of vapors displaced from a vehicular fuel tank during refueling.

(b) All tank gauging and sampling sites shall be made vapor-tight so as to prevent emissions except when gauging or sampling takes place. All pressure and vacuum test ports shall be above grade but not more than thirty-six inches above grade. All overfill drains shall be made vapor-tight. No remote vapor check valves shall be used on balance-type systems.

(c) No Stage II vapor recovery system shall be installed unless the system:

1. Meets the manufacturer’s plans and specifications; and

2. Is listed as certified by the State of California Air Resources Board in the document “Gasoline Marketing and Distribution Appendix D Phase II,” hereby adopted and incorporated by reference.

(d) Operating instructions shall be conspicuously posted in the gasoline dispensing area for the system in use at the facility. The instructions shall clearly describe how to fuel vehicles correctly with vapor recovery nozzles. The operating instructions shall include a warning that repeated attempts to continue dispensing, after the system has indicated that the vehicle fuel tank is full, may result in spillage or recirculation of gasoline. If a toll-free telephone number is provided by the Department or its agents for consumers to report problems or voice complaints, such number shall also be conspicuously posted.

(4) Compliance Schedules.

(a) Any gasoline dispensing facility which commenced construction after November 15, 1990, but before November 15, 1992, and which dispenses or has dispensed 10,000 gallons or more in any one month during or after 1991, must install a Stage II vapor recovery system by June 30, 1993, or within six months following the first month in which the 10,000 gallon-per-month threshold is exceeded, whichever is later.

(b) Any gasoline dispensing facility which was in operation or under construction on November 15, 1990, and which dispenses or has dispensed 100,000 gallons or more in any one month during or after 1991, must install a Stage II vapor recovery system by December 31, 1993, or within one year following the first month in which the 100,000 gallon-per-month threshold, whichever is later.

(c) Any gasoline dispensing facility which was in operation or under construction on November 15, 1990, and which dispenses or has dispensed 10,000 gallons or more in any one month during or after 1991, but not as much as 100,000 gallons, must install a Stage II vapor recovery system by November 15, 1994, or within two years following the first month in which the 10,000 gallon-per-month threshold is exceeded, whichever is later.

(d) Any gasoline dispensing facility which commences construction or undertakes a significant modification after November 15, 1992, must install a Stage II vapor recovery system prior to dispensing 10,000 gallons or more in any one month.

(5) Testing.

(a) Once any newly installed Stage II vapor recovery system is in operational condition and ready for use, testing to verify the proper installation and function of the entire system (both infrastructure plumbing and aboveground equipment) shall be conducted. Tests shall be conducted in accordance with the following test procedures as found in Appendix J of the EPA document, “Technical Guidance – Stage II Vapor Recovery Systems for Control of Vehicle Refueling Emissions at Gasoline Dispensing Facilities,” Vol. II (EPA-450/3-91-022b), November 1991, hereby adopted and incorporated by reference:

1. Bay Area Source Test Procedure ST-30, Leak Test Procedure, or San Diego Test Procedure TP-91-1, Pressure Decay/Leak Test Procedure;

2. Bay Area Source Test Procedure ST-27, Dynamic Back Pressure, or San Diego Test Procedure TP-91-2, Pressure Drop vs. Flow/Liquid Blockage Test Procedure; and

3. Bay Area Source Test Procedure ST-37, Liquid Removal Devices.

(b) Testing may be conducted by the Department or its agents or by an installation or testing company. In the case where a party other than the Department or its agents will be conducting the initially required testing, the owner or operator of the gasoline dispensing facility shall notify the Department or its agents at least seven days in advance as to when the testing will occur and what party will conduct the testing. The Department or its agents shall have the right to conduct the testing if it desires to do so.

(c) Recertification of the function of the Stage II vapor recovery system shall be performed at least every five years or upon system replacement or major system modification, whichever occurs first. The recertification shall include all functional tests that were required for the initial system certification. A major system modification is considered to be replacing, repairing, or upgrading 75 percent or more of a facility’s Stage II vapor recovery system.

(6) Recordkeeping. All records required to be kept pursuant to this rule shall, unless otherwise specified in the text of this rule, be maintained for two years and be available for inspection by the Department or its agents upon request at the gasoline dispensing facility. If records are not kept at the facility, they shall be made available at the facility or other location acceptable to the Department upon seven days’ notice. Records of the following are required:

(a) Gasoline quantities delivered to the facility.

(b) Gasoline quantities dispensed.

(c) Log of maintenance inspections of Stage II system components.

(d) Invoices or work orders of any repairs performed on Stage II system components.

(e) Results of any tests of the Stage II system and its components.

(f) Any permits issued by the Department or its agents for the operation of the gasoline dispensing facility and its Stage II system.

(7) System Maintenance.

(a) All Stage II vapor recovery systems shall be maintained in proper working order in accordance with the manufacturer’s specifications to ensure the integrity and efficiency of the systems. If the vapor recovery system or a component of the system contains a significant defect, the system or component shall be taken out of service. No person shall use or permit the use of that system or component until it has been repaired, replaced or adjusted. Minor defects, which do not significantly reduce the effectiveness of the system below 95 percent vapor recovery, such as very small holes, cracks, or gashes, must be repaired within seven days.

(b) Equipment defects that could significantly impair the effectiveness of the system and require that the system be taken out of service are:

1. The absence or disconnection of any component which is required to be used in the system as certified.

2. A vapor hose which is crimped or flattened such that the vapor passage is blocked or the pressure drop through the vapor hose exceeds the allowed pressure drop in the system as certified.

3. A nozzle boot or coaxial hose which is torn in one or more of the following manners:

a. Triangular-shaped or similar tear 1/2-inch or more to a side, or a hole 1/2-inch or more in diameter; or

b. Slit, 1-inch or more in length.

4. A faceplate or flexible cone which is damaged in the following manner:

a. For balance nozzles and for nozzles of aspirator or educator assist-type systems, damage such that the capability to achieve a seal with a fill-pipe interface is affected for 1/4 of the circumference of the faceplate (accumulated); or

b. For nozzles of those vacuum assist-type systems which use a flexible cone, damage such that more than 1/4 of the flexible cone is missing.

5. A nozzle shutoff mechanism which malfunctions in any manner.

6. Vapor return lines, including such components as swivels, swing-joints, and underground or aboveground piping, which malfunction or which are blocked or restricted such that pressure drops through the lines exceed the requirements of the system as certified.

7. A vapor processing unit which is inoperative.

8. A vacuum producing device which is inoperative.

9. Pressure/vacuum relief valves, vapor check valves, or Stage I dry breaks which are inoperative.

10. Any equipment defect which is identified in the CARB Executive Order(s) applicable to the system as substantially impairing the effectiveness of the system in reducing air contaminants.

11. Any other defect which could impair the effectiveness of the system to recover 95 percent by weight of the gasoline vapors displaced.

(c) All systems affected by the above defects are to be considered defective and shall be tagged “Out of Order.” Except during repair activity, the “Out of Order” tag shall not be removed, and the tagged equipment shall not be used, permitted to be used, or provided for use until it has been repaired, replaced, or adjusted as necessary.

(d) All replacement parts and parts used to retrofit existing dispensers for Stage II vapor recovery shall be original equipment manufacturer parts or aftermarket parts listed as described in paragraph 62-252.400(3)(c)2, F.A.C.

(e) All facilities subject to this rule shall provide the Department or its agents access to any and all components as necessary to determine compliance with the provisions of this rule.

(8) Training.

(a) The owner or operator of a gasoline dispensing facility subject to this rule shall ensure that at least one representative of the facility is knowledgeable about the operation and maintenance of the Stage II vapor recovery system in use at the facility.

(b) Information on the following subject areas shall be maintained by the owner or operator and, upon sale or transfer of the facility, be transferred to the new owner or operator:

1. Equipment operation and function specific to the facility's Stage II vapor recovery system;

2. Maintenance schedules and requirements for the facility's equipment; and

3. Equipment manufacturer contacts (names, addresses, and telephone numbers) for parts and service.

Specific Authority 403.061 FS. Law Implemented 403.021, 403.031, 403.061, 403.087 FS. History–New 2-2-93, Formerly 17-252.400, Amended 11-23-94.