64E-8.005 Operation and Maintenance.

(1) The following operating standards shall apply to permitted Limited Use Systems:

(a) All components shall function properly at all times.

(b) Should the system shut down, the supplier shall take steps to restore it immediately. The supplier shall alert all users in advance of maintenance that will cause pressure loss or water quality change.

(c) The supplier shall alert the county health department 24 hours in advance where possible, but no later than the next business day after any shutdown or treatment failure.

(d) Disinfection equipment shall maintain a free available chlorine residual between 0.2 milligrams per liter (mg/L) and 4.0 mg/L free available chlorine residual or 5.0 mg/L total chlorine residual throughout the entire system, or the equivalent of these limits as determined by the department. A functional disinfectant concentration test kit shall be kept on site at all times.

1. Where continuous disinfection is required, the supplier shall test the chlorine residual daily by using a N,N-Diethyl-p-Phenylenediamine (DPD) color comparison, or a portable spectrophotometer test kit and post the results in a log kept on premises. The department shall specify tests for alternative disinfectants upon construction approval.

2. Where continuous disinfection is required for a Limited Use Community System and a chemical disinfectant is used, the supplier shall assure a state certified water treatment plant operator services the system weekly.

(2) The following maintenance standards apply to all permitted systems:

(a) All components shall be in good repair and used as intended.

(b) Replacement of components shall be with new or like-new products, approved per subsection 64E-8.002(6), F.A.C., and equal to those originally approved.

(c) The vicinity within 5 feet of the system and well shall be free of vegetation, debris and hazards which could prevent or hinder inspection.

(d) If an emergency alteration occurs, the supplier must submit a completed Form DH 4092B to the department the next business day.

(e) The supplier shall post maintenance/repair dates and type in a log kept on the premises.

(f) Systems vulnerable to vandalism shall be secured, but any enclosure shall not restrict visibility or authorized access for inspection.

(g) The upper end of the well casing shall be watertight except for vents which shall be directed downward and protected with 20-mesh screen.

(h) Any chemical which could contaminate the water supply shall not be stored within 25 feet of the well head unless the chemical container is in an additional, above-ground containment structure capable of containing the full volume of the chemical.

Specific Authority 403.862(1)(f), 381.0011(4), (13), 381.006, 381.0062(1), (3)(a) FS. Law Implemented 381.0012, 381.006(1), (2), 381.0061, 381.0062, 381.0067, 403.862(1)(f) FS. History–New 1-1-93, Amended 8-20-96, Formerly 10D-4.028, Amended 1-26-98, 10-7-02.