# CHAPTER 59A-3

HOSPITAL LICENSURE

59A-3.065 	Definitions

59A-3.066 	Licensure Procedure

59A-3.077 	Fire Protection

59A-3.078 	Comprehensive Emergency Management Plan

59A-3.079 	Codes and Standards to Be Used for Construction of Hospitals

59A-3.080 	Plans Submission and Fee Requirements

59A-3.081 	Physical Plant Requirements for General, Rehabilitation and Psychiatric Hospitals

59A-3.110 	Services

59A-3.2085 	Department and Services

59A-3.250 	Surveillance, Prevention, and Control of Infection

59A-3.251 	Hospital Reporting of Exposure to Selected Infectious Diseases

59A-3.252 	Classification of Hospitals

59A-3.253 	Investigations and License, Life Safety and Validation Inspections

59A-3.254 	Patient Rights and Care

59A-3.255 	Emergency Care

59A-3.270 	Health Information Management

59A-3.271 	Quality Improvement

59A-3.272 	Governing Body

59A-3.273 	Management and Administration

59A-3.274 	Anatomical Gifts, Routine Inquiry

59A-3.275 	Organized Medical Staff

59A-3.276 	Maintenance

59A-3.277 	Functional Safety

59A-3.278 	Rehabilitation, Psychiatric and Substance Abuse Programs

59A-3.279 	Itemized Patient Bill

59A-3.280 	Child Abuse and Neglect

59A-3.281 	Spontaneous Fetal Demise

59A-3.300 	Licensure Procedure

59A-3.301 	Goals, Policies and Procedures

59A-3.302 	Personnel

59A-3.303 	Facilities and Physical Plant Safety

59A-3.312 	Exceptions (Repealed)

## 59A-3.065 Definitions.

In addition to definitions contained in Chapter 395, F.S., the following definitions shall apply specifically to hospitals, as used in Rules 59A-3.300-3.312, F.A.C.:

(1) “Accepted Medical Standards” means the current professional standards pursuant to Section 766.102, F.S., which are utilized by affiliated organ procurement organizations (OPO), tissue banks and eye banks to determine the suitability of organs, tissues, and eyes for the purposes of transplantation, medical research or instruction.

(2) “Accrediting organizations” means the Joint Commission on Accreditation of Healthcare Organizations, and the American Osteopathic Association.

(3) “Agency” means the Agency for Health Care Administration (AHCA).

(4) “Ambulatory care” means the delivery of care pertaining to non-emergency, adult, adolescent, and pediatric outpatient encounters, whether performed through the clinical departments of the hospital or an organized ambulatory program which is included as a component of the licensed hospital, regardless of the physical location of such services.

(5) “At or near the Time of Death” means that point in time in the care of the patient at which the procedures have begun for the determination and certification of brain death as defined under the provisions of Section 382.009, F.S., or cardiorespiratory (cardiac) death as defined under the provisions of subsection 59A-3.065, F.A.C.

(6) “Bassinet” means special accommodations with supporting services for newborn infants after transfer from the delivery or recovery suites. These accommodations are not considered hospital beds for licensing purposes except when part of an intensive neonatal care unit approved pursuant to Chapter 59C-1, F.A.C.

(7) “Biomedical waste” means any solid or liquid waste which may present a threat of infection to humans, as defined in Chapter 64E-16, F.A.C.

(8) “Brain Death” means the determination of death under provisions of Section 382.009, F.S., where there is irreversible cessation of the functioning of the entire brain, including the brain stem.

(9) “Cardiorespiratory Death” means the cessation of life which is manifested by the loss or absence of spontaneous heart beat and breathing.

(10) “Child abuse or neglect” means harm, pursuant to Section 39.01(32), F.S., or threatened harm to a child’s physical or mental health or welfare by the acts or omissions of a parent, adult household member, or other person responsible for the child’s welfare, or, for purposes of reporting requirements, by any person.

(11) “Child protection team” means a team of professionals established by the Department of Health and Rehabilitative Services to receive referrals from the single intake and protective services staff of the children, youth and families program and to provide specialized and supportive services to the program in processing child abuse and neglect cases. A child protection team shall provide consultation to other persons on child abuse and neglect cases pursuant to Section 39.303, F.S.

(12) “Continuous” means available at all times without cessation, breaks or interruption.

(13) “Dentist” means a doctor of dentistry legally authorized to practice under Chapter 466, F.S.

(14) “Designee or Requester” means a person or organization identified, designated, and delegated by the hospital administrator to carry out the provisions of this chapter and the responsibilities mandated by Section 765.522, F.S., and to make the request to the patient or next of kin for the donation of organs, tissues and eyes.

(15) “Diagnostic imaging” means those ionizing and non-ionizing radiological procedures, including but not limited to x-rays, and computerized tomographic scanning, requiring the supervision and expertise of a physician with appropriate training or experience.

(16) “Directly involved” for the purposes of reporting of adverse incidents to the agency means any employee or independent contractor of a hospital or member of a hospital’s medical staff who could exercise control over the event which is reportable as an adverse or untoward incident.

(17) “District intake counselor” means Department of Health and Rehabilitative Services’ staff responsible for the investigation of suspected abuse or neglect.

(18) “District Medical Examiner” means a physician who fills a position defined according to the provisions of Section 406.06, F.S.

(19) “Donation” means the free and voluntary gift of one or more organs, tissues or eyes for the purpose of medical research or transplant surgery.

(20) “Donor” means a person from whom organs, tissues or eyes have been surgically removed for the purpose of transplantation.

(21) “Emergency department” means for the purposes of Section 395.1041, F.S., any department of any general hospital when a request is made for emergency services and care for any emergency medical condition which is within the service capability of the hospital.

(22) “Emergency Medical Technician (EMT)” means any person who is certified as an EMT pursuant to Chapter 401, F.S.

(23) “Eye bank” means a public or private entity which is involved in the retrieval, processing or distribution of human eye tissue for transplantation and certified pursuant to Section 765.541, F.S. Funeral homes or direct disposers engaged solely in the retrieval of eye tissue are not considered an eye bank for these purposes.

(24) “Facilities” means those objects, including physical plant, equipment and supplies, necessary for providing required services.

(25) “General acute care hospital” means a general hospital which has an average length of stay of 25 days or less for all inpatient beds.

(26) “General hospital” means any facility which meets the provisions of subsection (29) and which regularly makes its facilities and services available to the general population.

(27) “Governing body” means the individual, agency, group or corporation appointed, elected, or otherwise designated, in which the ultimate responsibility and authority for the conduct of the hospital is vested.

(28) “Health professional” means a person specifically licensed to practice a health profession, or a person specifically trained to practice one or more aspects of a health profession by a school or program officially recognized by this State or accredited by a national accrediting organization.

(29) “Hospital” means any establishment that:

(a) Offers services more intensive than those required for room, board, personal services, and general nursing care, and offers facilities and beds for use beyond 24 hours by individuals requiring diagnosis, treatment, or care for illness, injury, deformity, infirmity, abnormality, disease or pregnancy; and

(b) Regularly makes available at least clinical laboratory services, diagnostic x-ray services, and treatment facilities for surgery or obstetrical care, or other definitive medical treatment of similar extent. However, the provisions of this chapter shall not apply to any institution conducted by or for the adherents of any well-recognized church or religious denomination that depends exclusively upon prayer or spiritual means to heal, care for, or treat any person.

(30) “Hospital emergency services” means: For the purposes of Section 395.1041, F.S., hospital emergency services are any services within the service capability of the hospital.

(31) “Inpatient beds” means accommodations with supporting services for patients who are admitted by physician order with the expectation that the patient would stay in excess of 24 hours and occupy a bed.

(32) “Intensive residential treatment programs for children and adolescents” means a specialty hospital accredited by the Joint Commission on Accreditation of Healthcare Organizations which provides 24-hour care and which has the primary functions of diagnosis and treatment of patients under the age of 18 having psychiatric disorders in order to restore them to an optimal level of functioning.

(33) “Licensed practical nurse” means one who is currently licensed in the state of Florida to practice practical nursing as defined in Chapter 464, F.S.

(34) “Long term care hospital” means a general hospital which:

(a) Meets the provisions of Section 395.002(12), F.S.;

(b) Has an average length of inpatient stay greater than 25 days for all hospital beds; and

(c) Meets the provisions of Rule 59C-1.002, F.A.C.

(35) “Medical Examiner’s Case” means any death occurring in the State and which is defined according to the provisions of Section 406.11, F.S.

(36) “Nursing services” means those services pertaining to the curative, restorative, and preventive aspects of nursing care that are performed or supervised by a registered professional nurse under the direction of a physician.

(37) “On duty” means personnel within the hospital, appropriately dressed, continuously alert and responsive to patient needs.

(38) “Operating room suite” means a room, or set of physically contiguous rooms located on the same floor, used primarily for the purpose of performing operations and other physically invasive procedures on patients, as well as rooms for surgical supply and disinfecting.

(39) “Organ” means a body part such as a heart, kidney, pancreas, liver, or lung that requires vascular reanastomosis.

(40) “Organ Procurement Organization” means a public or private entity designated as an OPO by the Secretary of the U.S. Department of Health and Human Services (HHS) which is engaged in the process of recovering organs for the purposes of transplantation and certified pursuant to Section 765.541, F.S.

(41) “Organized medical staff” means a formal organization of physicians and other health professionals approved by the governing body with the delegated responsibility to provide for the quality of all medical care, and other health care as appropriate, provided to patients, for planning for the improvement of that care, and for the ethical conduct and professional practices of its members. Nothing herein shall be construed to preclude a governing body from restricting membership on the organized medical staff to only those disciplines required to be included by Florida law.

(42) “Paramedic” means any person who is certified as a paramedic pursuant to Chapter 401, F.S.

(43) “Parts” means any organs, tissues, fluids or other portions of a human body including the organs or tissues described in subsections (34) and (57) of this section, as well as bone, arteries and blood.

(44) “Patient grievance” means any written complaint by a patient relating to patient care or the quality of medical services, except for those matters pertaining to the cost of care.

(45) “Pharmacist” means one who is licensed under Chapter 465, F.S., and engages in the practice of the profession of pharmacy.

(46) “Physician” means a doctor of medicine or osteopathy legally authorized to practice under the provisions of Chapter 458, F.S., or 459, F.S.

(47) “Podiatrist” means a person legally authorized to practice podiatry under Chapter 461, F.S.

(48) “Potential Donor” means any person approaching death or who has died in a Florida hospital and is deemed medically acceptable according to the medical standards of the affiliated OPO, tissue bank or eye bank for organ, tissue, or eye donation.

(49) “Premises” means those buildings, beds, and facilities located at the main address of the licensee and all other buildings, beds, and facilities for the provision of hospital care located in such reasonable proximity to the main address of the licensee as to appear to the public to be under the dominion and control of the licensee.

(50) “Provisional accreditation” means a determination by a hospital accrediting organization that substantial standards compliance deficiencies exist in a hospital.

(51) “Provisional license” means a restricted license issued to a hospital which does not meet requirements for a regular license, but is in substantial compliance with the pertinent statutes and rules.

(52) “Psychiatric hospital” means a Class III specialty hospital primarily restricted to treating persons whose sole diagnosis, or in the event of more than one diagnosis, the principal diagnosis, as defined in the Diagnostic and Statistical Manual of Mental Disorders (DSM III-R) is a psychiatric disorder, as defined in Rule 59C-1.040, F.A.C.

(53) “Psychiatric program” means psychiatric or substance abuse programs.

(54) “Qualified medical person” means for the purposes of Section 395.1041, F.S., the licensed individual responsible for the operation of the emergency services area during the time of a transfer.

(55) “Quality improvement program” means a program of ongoing activities designed to objectively and systematically evaluate the quality of patient care and services, pursue opportunities to improve patient care and services, and resolve identified problems which applies standards of patient care to evaluate the quality of the hospital’s performance.

(56) “Registered dietitian” means one who meets the standards and qualifications established by the Commission on Dietetic Registration of the American Dietetic Association and is currently registered with the American Dietetic Association.

(57) “Registered professional nurse” means one who is currently licensed in the State of Florida to practice professional nursing as defined in Chapter 464, F.S.

(58) “Regular license” means an unrestricted license issued to a hospital in recognition of compliance with rules and standards of these Rules and Chapter 395, F.S.

(59) “Rehabilitation hospital” means a Class III specialty hospital in which an organized program of integrated intensive care services is provided by a coordinated multidisciplinary team to patients with severe physical disabilities, as defined under paragraph 59C-1.039(2)(c), F.A.C.

(60) “Relieve or eliminate the emergency medical condition” means, for the purposes of Sections 395.002 and 395.1041, F.S., provision of care, treatment or surgery consistent with the applicable standard of care, by a physician, necessary to either eliminate the emergency medical condition or to eliminate the likelihood that the emergency medical condition will deteriorate or recur without further medical attention within a reasonable period of time.

(61) “Routine Inquiry Form” means a reporting document used to indicate that a request for donation of organs, tissues, or eyes was made.

(62) “Rural hospital” means a general hospital which meets the definition of Section 395.602(2)(e), F.S.

(63) “Selected Infectious Diseases” means Acquired Immunodeficiency Syndrome; anthrax; syphilis in an infectious stage; diphtheria; disseminated vaccinia; Hansen’s disease; hepatitis A; hepatitis B; hepatitis non-A, non-B; Legionnaire’s disease; malaria; measles; meningococcal meningitis; plague; poliomyelitis; psittacosis; pulmonary tuberculosis; Q fever; rabies; rubella; typhoid fever.

(64) “Special care unit” means a unit designated to provide acute care services, with a concentration of qualified professional staffing and supportive resources, to patients requiring extraordinary care on a concentrated and continuous 24-hour basis. Special care units include, but are not limited to burn, cardiac, cardiovascular surgery, neonatal, respiratory, renal care provided in the hospital, but not including ambulatory units, spinal injury units, trauma and multipurpose special care units, operating room suite, including medical-surgical intensive care or any combination of the above.

(65) “Specialty hospital” means any facility which meets the provisions of subsection (25), and which regularly makes available either:

(a) The range of medical services offered by general hospitals, but restricted of a defined age or gender group of the population;

(b) A restricted range of services appropriate to the diagnosis, care, and treatment of patients with specific categories of medical or psychiatric illnesses or disorders; or

(c) Intensive residential treatment programs for children and adolescents as defined in subsection (28).

(66) “Substance abuse hospital” means a Class III specialty hospital primarily restricted to treating persons whose sole diagnosis, or in the event of more than one diagnosis, the principal diagnosis, as defined in the Diagnostic and Statistical Manual of Mental Disorders is a substance abuse disorder defined under paragraph 59C-1.041(2)(u), F.A.C.

(67) “Tissue” means any non-visceral or non-vascularized collection of similar cells and their associated intercellular substances. There are four generally accepted basic body tissues:

(a) Epithelium (including corneal tissue);

(b) Connective tissues including blood, bone and cartilage;

(c) Muscle; and

(d) Nerve tissue.

(68) “Tissue Bank” means a public or private entity certified pursuant to Section 765.541, F.S., which is involved in at least one of the following activities:

(a) Procuring, processing, storing or distributing viable or nonviable human tissues to clinicians who are not involved in the procurement process;

(b) Procuring, processing, and storing human tissues in one institution and making these tissues available to clinicians in other institutions; or

(c) Procuring, processing, and storing human tissues for individual depositors and releasing these tissues to clinicians at the depositor’s request.

(69) “Transfer” means, for the purposes of Section 395.1041, F.S., the movement, including the discharge, of an individual from a hospital’s facilities at the direction of any person employed by, or affiliated or associated, directly or indirectly with, the hospital who has the authority to do so under the hospital’s policies and procedures, but does not include such a movement of an individual who has been declared dead or who leaves the facility without permission or against medical advice.

(70) “Transplantation” means the surgical grafting or implanting in its entirety or in part one or more tissues or organs taken from another person.

Rulemaking Authority 381.0031, 395.1025, 395.1055 FS. Law Implemented 381.006, 381.0098, 381.231, 395.001, 395.002, 395.1023, 395.1025, 395.1055, 408.035, 408.036, 415.503, 415.5055 FS. History–New 9-4-95, Formerly 59A-3.201.

## 59A-3.066 Licensure Procedure.

(1) No person or governmental unit shall establish, conduct, or maintain a hospital in this state without first obtaining a license.

(2) All persons requesting licensure for the operation of a hospital under the provisions of Chapter 395, F.S., shall make application to the agency, on forms provided, AHCA Form 3130-8003-January 1995, and AHCA Form 3130-8001-January 1995, and shall receive a regular or provisional license prior to the acceptance of patients for care or treatment.

(a) Each hospital applying for a license shall be designated by a distinctive name, and the name shall not be changed without first notifying the licensing agency and receiving approval in writing. Duplication of an existing hospital name is prohibited in new hospitals. The following documents shall be prepared at the time of the initial application, and shall be available for review by the agency at the initial licensure inspection:

1. Governing authority bylaws, rules and regulations, or other written organization plan;

2. Organized professional staff bylaws, rules and regulations;

3. The hospital’s fire and Comprehensive Emergency Management Plans;

4. Roster of organized medical staff members;

5. Nursing procedure manual; and

6. Roster of registered nurses, licensed practical nurses, emergency medical technicians and paramedics with current registration number.

(b) The following documents shall accompany the initial application:

1. The hospital’s zoning certificate;

2. Articles of incorporation;

3. Registration of a fictitious name;

4. The name and address of the ultimate owner of the hospital;

5. A valid certificate of need or letter of exemption as required by Sections 408.031 through 408.045, F.S.;

6. Approval for licensure from the agency’s Office of Plans and Construction; and

7. Evidence of medical malpractice insurance through the Patient Compensation Fund or other means of demonstrating financial responsibility as provided for under Chapter 766, F.S.

(c) All applications for change of ownership shall include:

1. A signed agreement to correct physical plant deficiencies listed in the most recent licensure inspection to conform to the most recently adopted, nationally recognized life-safety code, unless otherwise modified herein;

2. Written verification of the transaction, which must include an effective date and the signatures of both the buyer and the seller;

3. Registration of a fictitious name;

4. The name and address of the ultimate owner of the hospital;

5. Evidence of payment of, or arrangement to pay, any liability to the state pursuant to Section 395.003(3)(b)2., F.S., and

6. A valid certificate of need as specified in Sections 408.031 through 408.045, F.S., and Chapter 59C-1, F.A.C.

(d) An application for biennial licensure renewal must be accompanied by:

1. A copy of the hospital’s most recent accreditation report, if the hospital is accredited by an accrediting organization and the hospital seeks to substitute evidence of accreditation in lieu of an agency licensure inspection, and

2. Evidence of medical malpractice insurance through the Patient Compensation Fund or other means of demonstrating financial responsibility as provided for under Chapter 766, F.S.

(e) An application for the addition of beds or off-site outpatient facilities to a hospital’s license must include:

1. A valid certificate of need or letter of exemption as required by Sections 408.031 through 408.045, F.S., and

2. Approval from the agency's Office of Plans and Construction, pursuant to Rules 59A-3.077-.081, F.A.C.

(f) Evidence of medical malpractice insurance through the Patient Compensation Fund or other means of demonstrating financial responsibility as provided for under Chapter 766, F.S., must be submitted annually to the agency.

(g) Upon receipt of a completed initial application the agency shall conduct a survey of the facility to determine compliance with Chapter 395, F.S., Part I, and Rules 59A-3.077-.081 and 59A-3.066-.312, F.A.C.

(h) When the applicant and hospital are in compliance with Chapter 395, F.S., Part I and Rules 59A-3.077-3.081 and 59A-3.065-.312, F.A.C., and have received all approvals required by law, the agency shall issue a license.

(i) A single license will be issued to a licensee for facilities located on separate premises, upon request of the applicant. The license will specifically state the location of the facilities, their services, and the licensed beds available on each separate premises. Such a license shall also specifically identify the general or specialty classification of hospitals located on separate premises.

(3) A license fee of $1,500 per hospital, or $30 per licensed bed, whichever is greater, shall accompany an application for an initial, biennial renewal, or change of ownership license. An application for the addition of beds to a license shall be accompanied by a license fee of $30 per additional bed. All permanent additions to the constructed bed capacity occurring after the issuance of the license shall require licensure prior to occupancy effective the date surveyed and approved for occupancy, and require payment of the necessary additional fee on a per bed basis. The license fee shall be made payable to the Agency for Health Care Administration. No license shall be issued without payment of the requisite fee, and, if the request for licensure is withdrawn, the license fee is not refundable. Where licenses are denied in whole or part, the license fee is not refundable. Those hospitals operated by the Department of Health and Rehabilitative Services and the Department of Corrections are not required to pay a license fee.

(4)(a) In the event of a change in licensure classification, suspension or revocation of a license, or voluntary cessation of services which are required by Section 395.002(12), F.S., the facility license shall be returned to the agency by the licensee. A license returned to the agency will be terminated upon receipt by the agency, and the facility may not operate as a hospital until licensure is obtained. For continued operation, the licensee must apply for a new license in compliance with the requirements for initial licensure specified in this section, and subject to the provisions of the certificate of need program as specified in Sections 408.031-.045, F.S., and Chapter 59C-1, F.A.C.

(b) In the event of an intended change in ownership, as described in Section 395.003(3)(b)1., F.S., an application for a new license must be submitted at least 60 days prior to the change, consistent with the requirements of paragraph (2)(c) of this section.

(5) A licensee shall notify the agency of impending closure of a hospital 90 days prior to such closure. The hospital shall be responsible for advising the licensing agency as to the placement of patients and disposition of medical records.

(6) Each license shall specifically state the name of the licensed operator of the hospital, the class of hospital, and the name and location of the hospital. Any beds in the hospital which are regulated under the certificate of need program, as specified in Chapter 59C-1, F.A.C., shall be listed, including the number of licensed beds by type. The license for hospitals having facilities on more than one premises shall specifically state the location of each facility, their general or specialty classification, their services, and the licensed beds available on each separate premises.

(7) Licenses shall be posted in a conspicuous place on the licensed premises, and copies of licenses shall be made available for inspection to all persons. In the case of a single license issued for facilities on more than one premises, a copy of the license shall be retained and posted in a conspicuous place at each separate premises.

(8) A license, unless sooner suspended or revoked, shall automatically expire two years from date of issuance, and shall be renewable biennially upon application for renewal and payment of the fee prescribed by these rules, provided that the applicant and hospital meet the requirements established under the Chapter 395, Part I and Rules 59A-3.077-.081 and 59A-3.066-.312, F.A.C. Application for renewal of license shall be made not less than 90 days prior to expiration of a license, on forms provided by the Agency, AHCA Form 3130-8003-January 1995, and AHCA Form 3130-8001-January 1995. If an application is received after the required filing date and exhibits a hand-canceled postmark obtained from a United States Post Office or other postal carrier dated on or before the required filing date, no fine will be levied.

(9) The AHCA shall issue a provisional license for any hospital in substantial compliance with the statute and Rules 59A-3.077–3.081 and 59A-3.066-.312, F.A.C. Provisional licenses are issued only after the AHCA is satisfied that preparations are being made by the hospital to qualify for regular license, and that the health and safety of patients will not be endangered during the interim. Any new hospital will be issued a provisional license prior to opening date, provided plans and specifications for the building have been approved by the licensing agency and the hospital has been surveyed and found to meet construction standards and health and safety surveys.

(a) A provisional license shall be granted for a period of no more than one (1) year and shall expire automatically at the end of its term. A provisional license may not be renewed.

(b) A regular license may be issued after the proposed hospital becomes operational and a resurvey has been made to determine compliance with the rule set forth herein.

(10) No licensed facility shall continuously operate a number of hospital beds greater than the number indicated by the AHCA on the face of the license.

(11) Hospitals shall not lease a portion of their licensed beds to another entity or facility, except for hospices licensed pursuant to Chapter 400, Part IV, F.S.

(12) The collocation of any residential program on the premises of a licensed hospital requires prior approval from the agency, based on the following criteria:

(a) Health, safety, and welfare cannot be jeopardized for any individual;

(b) The essential needs of patients must be met; and

(c) The facility must be staffed to meet the essential needs of patients.

Rulemaking Authority 395.003, 395.004 FS. Law Implemented 395.003, 395.004, 395.1055, 408.035, 408.036 FS. History–New 9-4-95, Amended 6-18-96, Formerly 59A-3.203.

## 59A-3.077 Fire Protection.

(1) Each hospital shall provide fire protection through the elimination of fire hazards. All portions of the existing facility shall comply with the requirements of Chapter 13, Existing Health Care Occupancies, as written in the Code for Safety To Life From Fire in Buildings and Structures, published by The National Fire Protection Association (NFPA), known as the Life Safety Code. The edition shall be as described in Chapter 69A-3.012, F.A.C.

(2) All fires shall be reported by telephone to the Office of Plans and Construction by the next working day after the occurrence. This office will send a fire occurrence report to the facility which is to be completed and returned within 15 calendar days. All reports shall be complete and thorough and shall record the cause of the fire, the date and time of day it occurred, the location within the facility, how it was extinguished, any injuries which may have occurred and a description of the local fire department participation.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055 FS. History–New 1-1-77, Formerly 10D-28.77, 10D-28.077, Amended 1-16-87, 9-3-92.

## 59A-3.078 Comprehensive Emergency Management Plan.

(1) Each hospital shall develop and adopt a written comprehensive emergency management plan for emergency care during an internal or external disaster or an emergency, which is reviewed and updated annually.

(2) The emergency management plan shall be developed in conjunction with other agencies and providers of health care services within the local community pursuant to Section 252.32(2), F.S., and in accordance with the “Emergency Management Planning Criteria for Hospitals,” AHCA Form 3130-8005-September 94, which is incorporated by reference. At a minimum, the plan shall include:

(a) Provisions for internal and external disasters and emergencies, pursuant to Section 252.34, F.S.;

(b) A description of the hospital’s role in community wide emergency management plans;

(c) Information about how the hospital plans to implement specific procedures outlined in the hospital’s emergency management plan;

(d) Precautionary measures, including voluntary cessation of hospital admissions, to be taken by the hospital in preparation and response to warnings of inclement weather, or other potential emergency conditions;

(e) Provisions for the management of patients, including the discharge of all patients that meet discharge requirements, in the event of an evacuation order, at the direction of the hospital administrator, or when a determination is made by the agency that the condition of the facility or its support services is sufficient to render it a hazard to the health and safety of patients and staff, pursuant to Chapter 59A-3, F.A.C. Such provisions shall address moving patients within the hospital and relocating patients outside the hospital, including the roles and responsibilities of the physician and the hospital in the decision to move or relocate patients whose life or health is threatened;

(f) Education and training of personnel in carrying out their responsibilities in accordance with the adopted plan;

(g) A provision for coordinating with other hospitals that would receive relocated patients;

(h) Provisions for the management of staff, including the distribution and assignment of responsibilities and functions, and the assignment of staff to accompany those patients located at off-site locations;

(i) Provisions for the individual identification of patients, including the transfer of patient records;

(j) Provisions to ensure that a verification check will be made to ensure relocated patients arrive at designated hospitals;

(k) Provisions to ensure that medication needs will be reviewed and advance medication for relocated patients will be forwarded to respective hospitals, when permitted by existing supplies, and state and federal law;

(l) Provisions for essential care and services for patients who may be relocated to the facility during a disaster or an emergency, including staffing, supplies and identification of patients;

(m) Provisions for contacting relatives and necessary persons advising them of patient location changes. A procedure must also be established for responding to inquiries from patient families and the press;

(n) Provisions for the management of supplies, communications, power, emergency equipment, security, and the transfer of records;

(o) Provisions for coordination with designated agencies including the Red Cross and the county emergency management office; and

(p) Plans for the recovery phase of the operation, to be carried out as soon as possible.

(3) The plan, including the “Emergency Management Planning Criteria for Hospitals,” shall be submitted annually to the county emergency management agency for review and approval. A fee may be charged for the review of the plan as authorized by Sections 252.35(2)(l) and 252.38(1)(e), F.S.

(a) The county office of emergency management has 60 days in which to review and approve the plan, or advise the facility of necessary revisions. If the county emergency management agency advises the facility of necessary revisions to the plan, those revisions shall be made and the plan resubmitted to the county office of emergency management within 30 days of notification by the county emergency management agency.

(b) The county office of emergency management shall be the final administrative authority for emergency plans developed by hospitals.

(4) The hospital shall test the implementation of the emergency management plan semiannually, either in response to a disaster or an emergency or in a planned drill, and shall evaluate and document the hospital’s performance to the hospital’s safety committee. As an alternative, the hospital may test its plan with the frequency specified by the Joint Commission on Accreditation of Healthcare Organizations.

(5) The emergency management plan shall be located for immediate access by hospital staff.

(6) In the event a disaster or emergency conditions have been declared by the local emergency management authority, and the hospital does not evacuate the premises, a facility may provide emergency accommodations above the licensed capacity for patients. However, the following conditions must be met:

(a) The facility must report being over capacity and the conditions causing it to the agency area office within 48 hours or as soon as practical. As an alternative, the facility may report to the agency central office, Hospital and Outpatient Services Section, at (850) 487-2717;

(b) Life safety cannot be jeopardized for any individual;

(c) The essential needs of patients must be met; and

(d) The facility must be staffed to meet the essential needs of patients.

(7) If the hospital will be over capacity after the declared disaster or emergency situation ends, the agency shall approve the over capacity situation on a case-by-case basis using the following criteria:

(a) Life safety cannot be jeopardized for any individual;

(b) The essential needs of patients must be met; and

(c) The facility must be staffed to meet the essential needs of patients.

(8) If a facility evacuates during or after a disaster or an emergency situation, the facility shall not be reoccupied until a determination is made by the hospital administrator that the facility can meet the needs of the patients.

(9) A facility with significant structural damage shall relocate patients until approval is received from the agency’s Office of Plans and Construction that the facility can be safely reoccupied, pursuant to Rules 59A-3.077, 59A-3.079 and 59A-3.081, F.A.C.

(10) A facility that must evacuate the premises due to a disaster or emergency conditions shall report the evacuation to the agency area office within 48 hours or as soon as practical. The administrator or designee is responsible for knowing the location of all patients until the patient has been discharged from the facility. The names and location of patients relocated shall be provided to the local emergency management authority or it’s designee having responsibility for tracking the population at large. The licensee shall inform the agency area office of a contact person who will be available 24 hours a day, seven days a week, until the facility is reoccupied.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055(1)(c) FS. History–New 1-1-77, Formerly 10D-28.78, 10D-28.078, Amended 9-3-92, 12-28-94.

## 59A-3.079 Codes and Standards to Be Used for Construction of Hospitals.

(1) All construction of new hospitals and all construction of additions, alterations, refurbishing, renovations to and reconstruction of existing hospitals shall be in compliance with the following codes and standards:

(a) The building codes described in Rule 9B-3.047, F.A.C.;

(b) The fire codes described in Chapter 4A-3, F.A.C.;

(c) The handicap accessibility standards in Chapter 553, Part V, F.S.;

(d) Facilities must comply with the requirements of the federal Americans With Disabilities Act;

(e) The following National Fire Codes of the National Fire Protection Association (NFPA);

1. Chapter 37, Installation and Use of Stationary Combustion Engines and Gas Turbines (1990 edition),

2. Chapter 50, Bulk Oxygen Systems at Consumer Sites (1990 edition),

3. Chapter 70B, Electrical Equipment Maintenance (1990 edition),

4. Chapter 70E, Electrical Safety Requirements for Employee Workplaces (1988 edition),

5. Chapter 77, Static Electricity (1988 edition),

6. Chapter 78, Lightning Protection Code (1989 edition),

7. Chapter 99B, Hypobaric Facilities (1990 edition),

8. Chapter 110A, Stored Electrical Energy Emergency and Standby Power Systems (1989 edition),

9. Chapter 170, Fire Safety Symbols (1991 edition),

10. Chapter 262, Method of Test for Fire and Smoke Characteristics of Electrical Wires (1990 edition),

11. Chapter 321, Basic Classification of Flammable and Combustible Liquids (1987 edition),

12. Chapter 497M, Classification of Gases, Vapors and Ducts for Electrical Equipment in Hazardous (Classified) Locations (1991 edition),

13. Chapter 600, Private Fire Brigades (1986 edition),

14. Chapter 801, Facilities Handling Radioactive Materials (1991 edition),

15. Chapter 850, Fossil Fueled Steam and Combustion Turbine Electric Generating Plants (1990 edition);

(f) Fire, Smoke and Radiation Damper Installation Guide for HVAC Systems (1986), Sheet Metal and Air Conditioning Contractors National Association, Inc. (SMACNA);

(2) No building shall be converted to hospital use unless it complies with the standards and codes set forth herein and with the physical plant standards set forth in Rule 59A-3.081, F.A.C., Physical Plant Requirements.

(3) Buildings acquired or constructed for purposes of outpatient treatment or diagnosis and which are to be included under the hospital license, whether on the premises or off, shall comply with the applicable portions of this rule. This requirement includes modular and prefabricated buildings. The outpatient portion of these facilities will be reviewed as business occupancy, and outpatient surgery areas will be reviewed as ambulatory health care occupancy.

(4) Local codes which set more stringent standards or add additional requirements shall take precedence over these standards and requirements as set forth in this section. Contact the Office of Plans and Construction when conflicts occur.

(5) The Fire Safety Evaluation System as described in NFPA-101M shall not be used as design criteria for new construction. The requirements of this rule are the minimum requirements.

Rulemaking Authority 395.005 FS. Law Implemented 395.001, 395.005 FS. History–New 1-1-77, Formerly 10D-28.79, Amended 1-16-87, 11-23-88, Formerly 10D-28.079, Amended 9-3-92.

## 59A-3.080 Plans Submission and Fee Requirements.

(1) No construction work, including demolition, shall be started until prior written approval has been given by the Office of Plans and Construction. This includes all construction of new facilities and any and all additions, modifications or renovations to existing facilities. When demolition is necessary, demolition and egress plans shall be submitted to the Office of Plans and Construction for prior written approval. Upon approval, demolition is permitted prior to construction document submission.

(2) Construction shall begin within one year following the date of written approval of the construction documents by the Office of Plans and Construction; otherwise, reapproval of the construction documents shall be obtained. A new plan review fee shall be submitted with the resubmission.

(3) When construction is required, either for new buildings or additions, alterations or renovations to existing buildings, the plans and specifications shall be prepared and submitted to the Office of Plans and Construction for approval by a Florida-registered architect and a Florida-registered professional engineer.

(4) Major alterations and renovations requiring conformance with the physical plant standards for new hospitals are defined to constitute those elements affecting the structural integrity of the building, fire safety, any substantial change in the functional operation, or a change in the number of beds.

(a) Where modernization or replacement construction is done within an existing facility, all new work, additions or both shall comply with applicable sections of the codes. Where major structural elements make total compliance impractical or impossible, the licensee or potential licensee shall submit a request for a waiver to the Office of Plans and Construction.

1. In modernization projects and those projects which are making additions to existing facilities, only that portion of the total facility affected by the project shall comply with applicable sections of the codes covering new health care occupancies.

2. Existing portions of the facility which are not included in the modernization or renovation but are essential to the functioning of the complete facility, as well as existing areas which receive less than substantial amounts of new work, shall comply with the section of NFPA-101 for existing health care occupancies.

(b) When a building is converted from one type occupancy to another, it shall comply with the new occupancy requirements of the life safety and building codes. For the purpose of life safety, conversion from a hospital to a nursing home or vice versa is not considered a change in occupancy.

(c) When parts of an existing facility which are essential to the continued overall operation of the facility cannot comply with current standards, the licensee or potential licensee may submit a request for a temporary or permanent waiver to the Office of Plans and Construction.

(d) Modernization, alterations or both, including new additions, shall not diminish the safety level which existed prior to the start of the construction. It is not required that safety be retained which is in excess of that required for new facilities.

(e) Nothing in these standards shall be construed as restrictive to a facility which chooses to do work or alterations as part of a long-range, phased safety improvement plan. All hazards to life and safety and all areas of noncompliance with applicable codes and regulations are to be corrected in accordance with a plan of correction approved in advance by the Office of Plans and Construction.

(f) An ambulatory surgical center or a birth center may not be constructed or operated on the same premises as a hospital. A facility or building used for medical care, including a medical office building which is owned and operated by the licensee of a hospital, may be fully integrated with the hospital physical plant. If a fully integrated facility or building in operation or under construction on the effective date of this rule is subsequently transferred, the hospital licensee shall be solely responsible for either physical separation or assuring full compliance with all life safety codes. Any other facility or building used for medical care, including a medical office building, must be physically separated from the hospital and have clear, visible and readable signs denoting its separateness from the hospital. Physically separate means, at a minimum, separation by fire walls and distinct mechanical and electrical systems. This provision will not be applicable to any facility or building used for medical care, including an ambulatory surgical center, a birth center or a medical office building which is in operation or has received preliminary plan approval prior to the effective date of this rule.

(5) The initial submission of plans to the Office of Plans and Construction for any new project shall include a completed Plan Review Application Form, ACHA Form 3500-0011 Nov. 96, incorporated by reference and a valid Certificate of Need or written confirmation from the Agency’s Certificate of Need/Budget Review Office that the proposed construction is either exempt from certificate of need or that it is not subject to certificate of need. This information shall accompany the initial submission, and approval will not be granted for any project without certificate of need verification. Plan Review Applications incorporated by reference are available from the Office of Plans and Construction.

(6) Plans and specifications submitted for review shall be subject to a plan review fee. This fee is prescribed by Section 395.0163, F.S., and is as follows.

(a) The amount of the plan review fee for the portion of the review through the first revised construction document review shall not exceed 1 percent of the total estimated cost of the construction project. A cost estimate of the proposed construction shall be submitted by the Florida-registered architect or Florida-registered engineer who is the primary design professional for the project.

(b) An initial fee payment is due with the first submission of plans and specifications to the agency. This initial payment shall be 1 percent of the estimated construction cost or $10,000, whichever is less, but shall in no case be less than $2,000.00. A $2,000.00 portion of the initial fee payment is non-refundable.

(c) The agency shall also collect its actual cost on all subsequent portions of the plan reviews and construction inspections.

(d) All fees shall be paid by check made payable to the Treasurer, State of Florida, with the check noted and identified that it is for the agency’s Plans and Review Trust Fund. Fees will be accepted only from the licensee or prospective licensee.

(7) Plans and specifications shall be submitted in three stages.

(a) Stage I, schematic plans.

(b) Stage II, preliminary plans, design development drawings.

(c) Stage III, construction documents, including addenda and change orders.

(8) Stage I, Schematic Plans.

(a) At a minimum, the schematic plans shall include the following.

1. Single-line drawings of each floor shall show the relationship of the various activities or services to each other and the room arrangement in each. The function of each room or space shall be noted in or near the room or space. The proposed roads and walkways, service and entrance courts, parking, and orientation shall be shown on either a small plot plan or on the first floor plan. Provide a simple cross-section diagram showing the anticipated construction. Provide a schematic life safety plan showing smoke and fire compartments, exits, exit passageways and gross areas of smoke and fire compartments. Provide information as to which areas are sprinklered, both new and existing.

2. If the proposed construction is an addition or is otherwise related to existing buildings on the site, the schematic plans shall show the facilities and general arrangement of those buildings.

3. Provide a list of the services to be provided in the proposed construction.

4. Provide a schedule showing the total number of beds, types of bedrooms and types of ancillary spaces.

(9) Stage II, Preliminary Plans.

(a) At a minimum, the preliminary plans shall include the following.

1. Site Development Plans. Show existing grades and proposed improvements as required by the schematic submission. Provide building locating dimensions.

2. For new hospital construction, provide a vicinity map showing the major local highway intersections.

3. Architectural Plans.

a. Provide floor plans, 1/8-inch scale minimum, showing door swings, windows, case work and mill work, fixed equipment and plumbing fixtures. Indicate the function of each space.

b. Provide a large-scale plan of typical new bedrooms with a tabulation of gross and net square footage of each bedroom. Tabulate the size of the bedroom window glass.

c. Provide typical large-scale wall interior and exterior sections and the exterior building elevations.

d. Equipment which is not included in the construction contract but which requires mechanical or electrical service connections or construction modifications shall be identified to assure its coordination with the architectural, mechanical and electrical phases of construction.

4. Life Safety Plans.

a. Provide single-sheet floor plans showing fire and smoke compartmentation, all means of egress and all exit signs. Additionally, dimension the compartments, and calculate and tabulate exit units.

b. Show all sprinklered areas, fire extinguishers, fire alarm devices and pull station locations.

c. If the project is an addition, alteration or conversion of an existing building, fully developed life safety plans shall be submitted.

5. Mechanical Engineering Plans.

a. Provide a one-line diagram of the ventilating system with relative pressures of each space. Provide a written description and drawings of the anticipated smoke control system, passive or active, and a sequence of operation correlated with the life safety plans.

b. Provide the general location of all fire and smoke dampers, all duct smoke detectors and firestats.

c. If the building is sprinklered, provide the location of the sprinkler system risers and the point of connection for the fire sprinkler system. State the method of design for the existing and new fire sprinkler systems.

d. Provide the locations of all plumbing fixtures and other items of equipment requiring plumbing services and/or gas services.

e. Provide the locations of any fume, radiological or chemical hoods.

f. Provide the locations of all medical gas outlets.

g. Provide the locations and relative size of major items of mechanical equipment such as chillers, air handling units, fire pumps, medical gas storage, boilers, vacuum pumps, air compressors and fuel storage vessels.

h. Provide the locations of hazardous areas and the volume of products to be contained therein.

6. Electrical Engineering Drawings.

a. Provide a one-line diagram of normal and essential electrical power systems showing service transformers and entrances, switchboards, transfer switches, distribution feeders and over-current devices, panel boards and stepdown transformers. The diagram shall include a preliminary listing and description of new and existing, normal and emergency block loads, preliminary estimates of available short-circuit current at all new equipment and existing equipment serving any new equipment, short-circuit and withstand ratings of existing equipment serving new loads and any new or revised grounding requirements.

b. Show fire alarm zones and correlate with the life safety plan.

7. Outline Specifications. Outline specifications are to include a general description of the construction, including construction classification and ratings of components, interior finishes, general types and locations of acoustical material, floor coverings, electrical equipment, ventilating equipment and plumbing fixtures.

8. Whenever an existing building is to be converted to a health care facility, the general layout of spaces of the existing structure shall be submitted with the preliminary plans for the proposed facility.

9. Whenever an addition, alteration, renovation or remodeling to an existing facility is proposed, the general layout of spaces of the existing facility shall be submitted with the preliminary plans.

(10) Stage III, Construction Documents.

(a) The Stage III, construction documents shall be an extension of the Stage II, preliminary plan submission and shall provide a complete description of the contemplated construction. Construction documents shall be signed, sealed and dated and submitted for written approval to the Office of Plans and Construction by a Florida-registered architect and Florida-registered professional engineer. These documents shall consist of work related to civil, structural, mechanical and electrical engineering, fire protection, lightning protection, landscape architecture and all architectural work. A life safety plan shall be included. Provide typical large-scale details of all major interior and exterior walls and smoke walls, horizontal exits and exit passageways.

(b) Structural engineering drawings shall include all plans, schedules and details.

(c) Mechanical engineering drawings shall be complete and shall include fire protection working plans for sprinklered buildings and fire and smoke control plans. Mechanical engineering drawings shall depict completely the systems to be utilized, whether new or existing, from the point of system origination to its termination.

(d) Fire protection drawings, where applicable, shall include the existing system as necessary to define the new work. Systems designed using the pipe schedule method shall not be connected to systems designed by hydraulic methodology.

(e) Electrical engineering drawings shall describe complete power, lighting, alarm, communications and lightning protection systems and power system study. Provide specifications for the complete description of the aforementioned disciplines. All construction documents shall be well coordinated. It is specifically required that in the case of additions to existing institutions, the mechanical and electrical, especially existing essential electrical systems and all other pertinent conditions shall be a part of this submission.

(f) The power study shall include a fault study complete with calculations to demonstrate that over-current devices, transfer switches, switchboards, panel boards, motor controls, transformers and feeders are adequately sized to safely withstand available phase-to-phase and phase-to-ground faults. The study shall also include an analysis of generator performance under fault conditions and a coordination study resulting in the tabulation of settings for all over-current device adjustable trips, time delays, relays and ground fault coordination. This must be provided for all new equipment and existing equipment serving any new equipment. Power studies for renovations of existing distribution systems shall include only new equipment and existing equipment upstream to the normal and emergency sources of the new equipment. Renovations involving only branch circuit panel boards without modifications to the feeder shall not require a full power study; instead, the power study shall be limited to the calculation of new and existing loads of the branch circuit panel.

(g) All subsequent addenda, change orders, field orders and other documents altering the above must also be signed, sealed and dated and submitted in advance to the Office of Plans and Construction for written approval.

(h) The construction documents shall contain comprehensive ceiling plans which show all utilities, lighting fixtures, smoke detectors, ventilation devices, sprinkler head locations and fire-rated ceiling suspension member locations where applicable.

(i) Floor/ceiling and roof/ceiling assembly descriptions shall be shown on all construction documents.

(j) Details and other instructions to the contractor shall be provided on the construction documents showing the techniques to be used to seal floor construction holes to the extent necessary to prevent smoke migration from floor to floor during a fire.

(k) Stage III, construction document submissions will be acted upon by the agency within 60 days of the receipt of properly executed construction documents and the initial payment of the plan review fee. Within this time frame, the department will either approve or disapprove the construction documents and shall provide a listing of deficiencies. Each subsequent resubmission of documents for review on the project will initiate another 60-day response period. The cost of additional reviews by the department will be applied against the plan review fee.

(11) Record Drawings. Within 90 days after occupancy of the building or a project involving a portion thereof, the licensee and the Office of Plans and Construction shall be provided with a complete set of legible drawings showing construction, fixed equipment and the mechanical and electrical systems as installed. These drawings shall include the life safety plans.

Rulemaking Authority 395.1055 FS. Law Implemented 395.0163, 395.1055 FS. History–New 1-1-77, Amended 4-26-78, Formerly 10D-28.80, Amended 1-16-87, 11-23-88, Formerly 10D-28.080, Amended 9-3-92, 6-29-97.

## 59A-3.081 Physical Plant Requirements for General, Rehabilitation and Psychiatric Hospitals.

(1) The following minimum standards of construction and specified minimum essential facilities to be included in hospitals shall apply to all new hospital construction, and all additions, alterations or renovations to an existing hospital on the effective date of these rules. Construction work in process on the effective date of these rules shall conform to the requirements in effect on the date the Stage II preliminary plans were approved.

(2) Site Work.

(a) The site shall be well drained, and all roads and parking areas shall be paved. The design of the road system shall provide access to all entrances, including docks for loading and unloading delivery trucks. Hospitals having an organized emergency services department shall have emergency access that is well marked to facilitate entry from the public roads or streets serving the site. Access to the emergency entrance shall not conflict with other vehicular or pedestrian traffic. Paved sidewalks shall be provided for pedestrian traffic. Parking and ease-of-entry considerations for the handicapped shall be required at all entrances designated for visitors and employees.

(3) The following requirements shall apply to the medical, surgical and postpartum nursing care units. The requirements for other special care areas, recovery rooms, intensive care rooms, critical care units and pediatric units can be found under descriptions of those units.

(a) Patient Rooms.

1. Private and multi-bed rooms shall be provided to meet the needs of patients in the hospital. The maximum room capacity shall be four patients. The minimum room areas, exclusive of toilet rooms, closets, lockers, wardrobes, vestibules and door swing areas shall be 100 square feet per patient in single-bed rooms and 80 square feet per patient in multi-bed rooms. In multi-bed rooms, a minimum clearance of 3 feet 8 inches shall be available at the foot of each bed to permit the passage of equipment and beds. A minimum clearance of 3 feet shall be provided between beds and between the bed and the side wall. For planning purposes, a full-size bed is assumed to be 3 feet 6 inches by 7 feet 0 inches.

2. In multi-bed rooms, visual privacy shall be provided for each patient by the installation of flame retardant cubicle curtains or the equivalent built-in devices. The design for privacy shall not restrict patient access to the entrance, lavatory, toilet, wardrobe or closet, nor shall it block the spray from fire sprinklers. To prevent interference with fire sprinkler spray patterns, cubicle curtains shall be provided with 1/2-inch square mesh at the top or the curtain shall be suspended on bead chains. See NFPA-13 for open area requirements.

3. A lavatory complete with mixing faucet shall be provided in each patient room or patient room toilet, each patient room without an exclusive toilet room, and in patient bedrooms containing three or more beds. Postpartum bedrooms must have a lavatory in each bedroom.

4. Each patient shall have within the room a separate locker or closet suitable for hanging full-length garments and for storing personal effects.

5. Each patient bedroom shall have direct access to a toilet room without going through the general corridor. One toilet facility shall serve no more than four beds.

6. If an isolation room is provided, it shall be equipped with a connecting toilet and bathing facility. A mask and glove station and a hand washing facility shall be provided in the anteroom or directly outside of the isolation room in an alcove if an anteroom is not provided.

(b) Service Areas. Each nursing care unit shall contain the following service areas.

1. There shall be a nurse station for charting by the nurses and doctors, for communication and for storage of administrative supplies. The nurse station area shall include the following facilities.

a. There shall be a hand washing facility near the nurse station. One lavatory may serve several areas if conveniently accessible to each.

b. There shall be a staff toilet room adjacent to the nurse station.

c. There shall be a staff lounge and/or conference room.

2. There shall be a clean workroom or clean holding room for storage and distribution of clean supply materials. If the room is used for preparing patient care items, it shall contain a counter and hand washing and storage facilities. If the room is used only for storage and holding as a part of a system for distribution of clean and sterile supply materials, the work counter and hand washing requirements may be omitted. The minimum size shall be 60 square feet.

3. There shall be an equipment storage room. This storage room may serve more than one nursing unit when it is conveniently located for access by each unit. The equipment storage room may be part of the clean workroom. If this option is used, the room size shall be increased by 5 square feet per bed served or a minimum size of 100 square feet, whichever is larger.

4. There shall be a soiled workroom. This room shall contain a flushing rim clinical service sink with 6-inch wrist blades and bedpan flushing device and a counter with a minimum work surface area of 6 square feet. The counter shall contain a double compartment sink. Where patient toilet rooms have bedpan rinsing devices, flushing rim clinical sinks will not be required. Rooms used only for the temporary holding of soiled materials need contain only a hand washing facility. The minimum size shall be 80 square feet.

5. There shall be a locked medicine room adjacent to the nurse station which shall be equipped with a sink, a refrigerator, locked storage and facilities for the administration of medication. The minimum area shall be 50 square feet. If drug distribution is from a self-contained unit dose cart or by other means as approved by the governing body of the hospital, the cart may be kept in a dedicated alcove in the nurse station provided it is under the visual control of the nursing staff. Medicine preparation may be part of the clean workroom, in which case an additional 20 square feet dedicated for this purpose shall be required. A refrigerator shall also be required if medicine preparation is included in this room.

6. There shall be a designated area for storage of clean linen. This area may be located within the clean workroom. Storage of clean linens, even a closed cart system, shall not be in an alcove off the corridor.

7. There shall be a nourishment room which shall contain a sink, a refrigerator, storage cabinets and equipment for serving nourishments between scheduled meals.

8. There shall be a dispensing type ice machine to provide ice for treatments and nourishment. Ice making equipment may be in the clean workroom or at the nourishment rooms under the control of the staff.

9. There shall be an alcove for the storage of stretchers and wheelchairs.

10. When individual bathing facilities are not provided for each patient bedroom, there shall be a minimum of 1 shower or tub for every 12 beds or fraction thereof. Each tub or shower shall be in an individual room or enclosure which provides privacy for bathing, drying and dressing. One sitz bath and one roll-in shower, including space for an attendant, shall be provided for patients at a ratio of 1 per every 100 beds or fraction thereof. This may be located on a separate floor.

11. There shall be an emergency equipment storage alcove. Space shall be provided for storing emergency equipment such as a cardiopulmonary resuscitation (CPR) cart. This area shall be under the direct control of the nursing staff and shall be located in close proximity to the nurse station but out of normal traffic.

12. There shall be a janitor closet for each nurse station. Each janitor closet shall contain a service sink or floor receptor and provisions for the storing of janitorial supplies.

(4) When intensive care units are provided, the following requirements shall be met.

(a) The location shall be convenient for access from emergency, respiratory therapy, laboratory, radiology and surgery.

(b) The location shall be arranged to eliminate the need for through traffic.

(c) The nurse station shall have space for charting and monitoring and shall be located so that nurses shall have visual control of each patient from common spaces.

(d) A nurse call system shall be provided at each bed for summoning assistance. The call system for the unit shall include provisions for an emergency code resuscitative alarm to summon assistance from outside the intensive care unit.

(e) Each bed shall be provided with one outside operable window. The minimum size of the window shall be 10 square feet of glass area.

(f) Each patient bed area shall include provisions for visual privacy to prevent casual observation by other patients and visitors.

(g) Separate rooms for single patient use shall contain a minimum net usable area of 120 square feet; multiple bed spaces using cubical curtain separators shall contain a minimum net usable area of 100 square feet per bed. The minimum room dimension perpendicular to the head wall shall be 12 feet.

(h) When private rooms or cubicles are provided, borrowed light shall have drapes or curtains which may be closed. Doors to these spaces shall be a minimum of 3 feet 8 inches wide and shall be arranged so as to minimize interference with movement of beds and large equipment.

(i) Sliding doors may be used for access to cubicles within a suite provided the outside door has a side-hinged breakaway feature that swings in the direction of egress and the hardware used eliminates the possibility of jamming and that any floor tracks do not impede wheel traffic or present a tripping hazard. When intensive care unit rooms are located on an exit access corridor, the sliding doors must be smoke resistant and may have the breakaway feature swing into the room.

(j) At least one private room or cubicle shall be provided in each intensive care unit for patients requiring isolation or separation.

(k) A space shall be provided for emergency cardiopulmonary resuscitation carts. This space shall be out of and not interfere with normal traffic in the unit.

(l) Each intensive care unit shall have a medication administration station or unit dose cart under staff control with locked storage for controlled drugs. The station or unit dose cart shall provide for emergency drugs as well as routine medication.

(m) If the intensive care unit is in excess of 5,000 square feet, it shall be designed with a corridor system and the medication dispensing station must be in a room.

(n) Each intensive care unit shall have staff hand washing facilities convenient to the nurse station and the area served. There shall be at least one lavatory for every three patient beds in open plan areas and one in each patient room or cubicle.

(o) The following additional service spaces shall be immediately available within each intensive care unit. These services may be shared by more than one intensive care unit if direct access is available from each intensive care unit suite.

1. There shall be a soiled workroom with a flushing rim clinical service sink with bedpan flushing device or the equivalent, and hand washing facilities. If each patient bed space has direct access to a patient toilet with a bedpan rinsing device, the requirement for the flushing rim clinical service sink with bedpan flushing device in the soiled workroom may be disregarded.

2. There shall be a separate space for the storage and distribution of clean medical and surgical supplies.

3. There shall be a clean linen closet or linen cart alcove.

4. There shall be a nourishment station, including a refrigerator, storage cabinets, ice dispenser and equipment for heating food and drinks.

5. There shall be a room or an alcove designated for the storage of equipment used in patient care areas. This room or alcove shall not interfere with the flow of traffic.

6. Portable commodes may be utilized in lieu of individual room toilets, but provisions shall be made for user privacy, storage, servicing and odor control.

7. There shall be purse lockers at each nurse station for the secure storage of staff's personal effects.

8. There shall be a janitor closet with floor receptor or service sink and storage space for janitorial cleaning equipment and supplies.

9. There shall be a staff toilet which may be in conjunction with the staff lounge. One staff lounge may serve several intensive care units.

10. There shall be a visitor waiting room for the unit, or units, with convenient access to telephones, drinking fountains and toilets. Such waiting rooms may serve several intensive care units.

(5) The following are additional special requirements for coronary intensive care.

(a) Each cardiac patient shall have a private room or enclosure for acoustical and visual privacy.

(b) Each cardiac patient shall have access to a toilet directly from the room or cubicle.

(6) Neonatal care facilities shall meet all of the following requirements.

(a) General Requirements.

1. General categories of neonatal services are Level I, newborn nursery; Level II, intermediate care; and Level III, intensive care. Facilities which offer obstetrical services shall provide a Level I newborn nursery or a holding nursery. See subparagraph 59A-3.081(10)(a)6., F.A.C. Existing hospitals which have Levels I, II or III services may continue to function without modifying existing facilities. Hospitals that remodel or build new Levels I, II or III nurseries shall comply with the requirements set forth hereinafter.

2. Those facilities providing obstetrical services but not Level I neonatal care shall provide a holding nursery for maternal respite. The postpartum rooms shall be designed for rooming-in capabilities. The holding nursery shall be immediately adjacent to the postpartum nurse station and shall be a minimum of 24 square feet per bassinet. The area shall contain a hand washing facility, a nurse call duty station and a vision panel to accommodate vision from the nurse station.

3. General room illumination shall provide a maximum of 100 footcandles. The lighting fixture layout shall be designed to avoid a fixture directly over the neonate.

4. All nurseries shall be provided with ceiling air supply and returns at or near the floor. Ventilation shall be designed to avoid a draft over the neonate.

5. A janitor closet shall be provided which has a floor receptor to serve new Levels I, II and III nurseries.

(b) Level I, newborn nurseries, shall meet the following requirements.

1. There shall be a minimum of 24 square feet of floor area for each bassinet.

2. There shall be a minimum of 3 feet between bassinets and between a bassinet and any fixed equipment or side wall.

3. There shall be no more than 24 bassinets per room.

4. There shall be a hand washing facility at each entrance to the nursery unit. A large diameter clock with a sweep second hand shall be provided in each nursery.

5. There shall be a minimum of one hand washing facility for every six bassinets or portion thereof. These hand washing facilities shall be evenly distributed within the nursery.

6. There shall be a workroom or work corridor for each nursery. The workroom shall contain a work counter, space for storing daily supplies, space for charting and view windows for observing the nursery. One workroom may serve more than one nursery. The following shall be provided immediately adjacent to the workroom or work corridor:

a. A staff toilet;

b. A soiled holding room with a minimum of 10 square feet of counter area and a double compartment sink. This room shall be accessible from both the public corridor and the workroom or work corridor; and

c. An equipment storage area with a minimum of 6 square feet of floor space for each patient station.

7. There shall be no doorways between adjacent nurseries. Doorways in nurseries are permitted only between the nursery and the workroom and between the nursery and the corridor.

8. There shall be at least one duplex electrical receptacle for every two parallel adjacent patient stations. The minimum spacing shall be 3 feet on center.

9. There shall be at least one oxygen, one medical air and one vacuum station for every six neonatal stations. These are to be evenly distributed within the nursery.

(c) Level II, intermediate care nurseries, shall meet the following requirements.

1. There shall be a minimum of 50 net square feet for each neonatal station.

2. There shall be a scrub and gown area at each entrance to the unit. This area shall be equipped with a minimum of two scrub sinks and gowning supply and disposal facilities.

3. There shall be a minimum of 4 feet between neonatal care isolettes and between a platform and fixed equipment or a side wall. There shall be 8 feet, foot to foot, between rows of isolettes in their normal positions.

4. There shall be a hand washing facility for every four neonatal stations or portion thereof and shall be conveniently located and evenly distributed.

5. There shall be a work counter at each neonatal care station at approximately the height of the platform mattress. The shelf shall be the width of the station. To accommodate the monitoring equipment, there shall be a shelf or other device at eye level. Sixty inches above the floor is suggested. The apron of the lower shelf shall accommodate oxygen, vacuum and compressed air.

6. There shall be a clean utility room for each nursery. The room shall contain a work counter and sink and space for storage of daily supplies. At the hospital’s discretion, this area may be replaced by storage areas and clean work surfaces in the nursery.

7. There shall be a control center in a location that offers a view of all of the neonatal stations.

8. There shall be charting and dictation space for physicians.

9. There shall be a medication preparation room with a minimum area of 50 square feet. The room shall contain a work counter, a sink and a refrigerator.

10. There shall be a multipurpose room for breast feeding demonstration and counseling with a minimum area of 80 square feet. The room shall be equipped with a hand washing facility.

11. There shall be a soiled holding room with a counter with a double compartment sink and a minimum of 10 square feet of counter area. This room shall be accessible from both the public corridor and the work/neonatal work areas.

12. There shall be a blood gas station.

13. Access to the Level II nursery suite is permitted only through exit access corridor doorways.

14. There shall be a lounge, a locker room and a toilet within or adjacent to the suite for staff use.

15. There shall be an equipment storage room with a minimum area of 18 square feet per neonatal station.

16. There shall be a minimum of four duplex electrical receptacles for each patient station. Two shall be connected to the critical branch of the essential electrical system with at least one of the required number connected to a dedicated circuit. Two receptacles shall be connected to a normal power circuit. There shall not be more than four receptacles per circuit. All branch circuits from the emergency system shall be from the same panel board. All branch circuits from the normal system shall be from the same panel board. Emergency system and normal system receptacles shall be identified and shall also indicate the panel board and circuit numbers. Both normal and emergency branch circuit over-current devices shall be readily accessible to nursing and other authorized personnel. Install one of the receptacles at the monitoring level, one above the main counter and two in the apron of the cabinet.

17. There shall be two oxygen, two medical air and two vacuum outlets per patient station.

(d) Level III, intensive care nurseries, shall meet all of the Level II, intermediate care nursery, requirements and the following modifications and additions.

1. There shall be a minimum of 80 net square feet for each high-risk neonatal station.

2. There shall be a minimum of 6 feet between neonatal care platforms and between a platform and fixed equipment or a side wall. There shall be 8 feet, foot to foot, between rows of isolettes in their normal positions.

3. There shall be an area out of normal traffic paths for storage of a portable x-ray machine.

4. There shall be a blood gas station.

5. There shall be a physicians’ sleeping room equipped with a private toilet and shower room.

6. There shall be a respiratory therapy workroom with a minimum area of 120 square feet. This may be located in the respiratory department provided a dedicated area is provided for neonatology.

7. There shall be a minimum of six duplex electrical receptacles for each patient station. Four shall be connected to the critical branch of the essential electrical system with at least two of the required number connected to dedicated circuits. Two receptacles shall be connected to a normal power circuit. There shall not be more than two receptacles per circuit. All branch circuits from the emergency system shall be from the same panel board. All branch circuits from the normal system shall be from the same panel board. Emergency system and normal system receptacles shall be identified and shall also indicate the panel board and circuit numbers. Branch circuit over-current devices shall be readily accessible to nursing and other authorized personnel. Install two of the receptacles above the top shelf, two above the main counter and four in the apron of the cabinet.

8. There shall be two oxygen, two medical air and two vacuum outlets per patient station.

(7) Pediatric Nursing Unit.

(a) The spatial requirements which apply to patient bedrooms shall also apply to pediatric and adolescent nursing units. Additional provisions for parental hygiene, toilet, sleeping and personal belongings shall be included in facilities where parents will be allowed to remain with young children.

(b) There shall be an examination and treatment room which shall be a minimum of 120 square feet in area. It shall contain a work counter, storage facilities and a hand washing facility.

(c) The service areas in pediatric and adolescent nursing units shall conform to the same requirements as for acute care areas.

(d) There shall be a minimum of one isolation room in each pediatric unit.

(e) There shall be an equipment storage room for each unit which shall contain a minimum of 10 square feet of storage space for each pediatric bed.

(f) There shall be a playroom with a minimum size of 250 square feet.

(8) Surgical Facilities.

(a) The number of operating rooms and recovery beds and the sizes of the service areas shall be based on the anticipated surgical workload. The surgical suite shall be located and arranged to prevent non-related traffic through the suite. Additions to and adaptations of the following elements and requirements shall be made for the special procedure operating rooms found in larger facilities. Care shall be exercised in the location of the rooms to be used for surgical cystoscopic and other endoscopic procedures so that cross traffic is minimized.

(b) Each general surgery room shall have a minimum clear area of 360 square feet exclusive of fixed cabinets and built-in shelves. Each room shall contain a telephone and an x-ray film illuminator capable of illuminating a minimum of two standard size films simultaneously.

(c) Operating rooms specifically intended for orthopedic surgery shall have an adjacent room for the storage of splints and traction equipment. If plaster of paris is used for cast work, there shall be a sink with a plaster trap. If a case cart system is utilized and the carts are to be stored elsewhere within the unit, this requirement will be waived.

(d) Operating rooms for the specific use of surgical cystoscopic and other endoscopic procedures shall have a minimum clear area of 250 square feet exclusive of fixed cabinets and built-in shelves. These rooms shall be located within the surgical department in such a manner as to minimize the distance between them and the recovery room, the main entrance and the staff lounge.

(e) Each recovery room shall contain a medication administration station, hand washing facilities, a nurse station with charting facilities, a flushing rim clinical service sink, and storage space for stretchers, supplies and equipment. The design shall provide space for additional equipment and shall provide a minimum of 3 feet between the patient recovery beds and adjacent wall surfaces. There shall be space and equipment for recovery beds at a ratio of 1-1/2 beds for each operating room. In facilities anticipating 1,000 or more surgical procedures per year, separate and additional recovery space will be necessary to accommodate surgical outpatients. There shall be an isolation room in the recovery room.

(f) Service Areas.

1. There shall be a control station which is located to permit visual observation of all traffic into and within the suite.

2. There shall be a surgical director’s office which is located to allow visitors to the suite to confer with the director without passage through the suite or the sterile quarters.

3. There shall be a minimum of one high-speed sterilizer conveniently located to serve all operating rooms.

4. There shall be two scrub positions which are located near the entrance to each operating room. Two scrub positions may serve two operating rooms if both are located adjacent to the entrance of both operating rooms. Scrub facilities shall be arranged to minimize any incidental splatter on nearby personnel or on medical equipment or supplies, and sufficient space shall be provided around the scrub facilities to eliminate any incidental contact with other surfaces by the medical personnel.

5. There shall be a soiled workroom for the exclusive use of the surgical suite staff, or there shall be a soiled holding room that is part of the system for the collection and disposal of soiled material. The soiled workroom shall contain a flushing rim clinical service sink, a work counter with a minimum area of 10 square feet and a double compartment sink, a waste receptacle and linen receptacle. When a soiled holding room is used, the flushing rim clinical service sink and work counter may be omitted. If this technique is chosen, a separate fluid waste disposal room will be required. The soiled work or storage facilities, or the fluid waste disposal facility, shall not have direct connection with operating rooms but shall open only to the sterile corridor.

6. There shall be a clean workroom. This workroom is required when clean materials are assembled within the surgical suite prior to use. A clean workroom shall contain a work counter with a minimum area of 14 square feet, a sink equipped for hand washing and a space for clean and sterile supplies. If a clean holding room is the technique desired by the hospital, the counter may be eliminated and a lavatory substituted for the sink.

7. There shall be an anesthesia workroom for cleaning, testing and storing anesthesia equipment. This workroom shall contain a work counter with a minimum area of 10 square feet and a sink equipped for hand washing.

8. There shall be an equipment storage room. This room is for the equipment and supplies to be used in the surgical suite and shall have a minimum area of 100 square feet.

9. There shall be clothing change areas for male and female personnel. The areas shall contain lockers, shower, toilets, urinals, lavatories equipped for hand washing and space for donning scrub surgical attire. These areas shall be arranged to require a one-way traffic pattern so that personnel entering from the outside of the surgical suite can change and move directly into the sterile corridor of the surgical suite.

10. There shall be a staff lounge and toilet facilities. Separate or combined lounges for male and female staff shall be provided. The lounge shall be designed to minimize the need to leave the suite and shall have convenient access to the recovery room.

11. There shall be areas for dictation and report preparation which shall be accessible from the lounge area.

12. There shall be a janitor closet in both the sterile and non-sterile areas. Each shall contain a floor receptor or service sink and storage for janitorial supplies and equipment.

(9) Outpatient Surgery.

(a) There shall be a separate area where outpatients may change from street clothing into hospital gowns and be prepared for surgery. This would include male and female locker rooms, toilets, clothing change or gowning areas. A common waiting room shall be provided. This function may be accommodated in the patient bedroom area.

(b) There shall be an outpatient recovery room. The recovery room may be part of the inpatient recovery area.

1. If a separate recovery room is provided, it shall accommodate a minimum of two recovery beds for each operating room. The size of the room shall be based on a minimum of 80 square feet per recovery bed.

2. There shall be a work counter and a hand washing facility.

(c) There shall be toilet rooms for patients with direct access from the outpatient recovery area. Smaller facilities may use the same spaces as for preoperative preparation.

(d) Outpatient surgical operating rooms shall have a minimum clear area of 170 square feet.

(e) If outpatient surgery is provided but not contiguous with the surgical department, all of the following requirements shall be met.

1. There shall be a control station located to permit visual observation of all traffic into and within the suite.

2. There shall be a surgical director's office which shall be located to allow visitors to the suite to confer with the director without passing through the suite or through the sterile quarters.

3. There shall be at least one high-speed sterilizer conveniently located to serve all operating rooms.

4. There shall be two scrub positions near the entrance to each operating room. Two scrub positions may serve two operating rooms if both are located adjacent to the entrance of each operating room. Scrub facilities shall be arranged so as to minimize any incidental splatter on nearby personnel, medical equipment or supplies, and sufficient space shall be provided around the scrub facilities to eliminate any incidental contact with other surfaces by the medical personnel.

5. There shall be a soiled workroom or decontamination room for the exclusive use of the surgical suite staff, or a soiled holding room that is part of the system, for the collection and disposal of soiled material.

a. The soiled workroom shall contain a flushing rim clinical service sink with a rinsing device, a work counter with a minimum area of 10 square feet, a double compartment sink with equipment for hand washing, a waste receptacle and a linen receptacle.

b. When a soiled holding room is used, the flushing rim clinical service sink and work counter may be omitted and a lavatory for hand washing substituted.

c. The soiled work or holding facilities shall not have direct connection with the operating rooms but shall open only into the sterile corridor.

6. There shall be a clean workroom. This workroom is required when clean materials are assembled within the surgical suite prior to use.

a. A clean workroom shall contain a work counter with a minimum of 14 square feet, a sink equipped for hand washing and space for clean and sterile supplies.

b. If a clean holding room is utilized by the hospital, the counter may be eliminated and a lavatory substituted for the sink.

7. There shall be an equipment storage room for storing supplies and equipment to be used in the surgical suite. The minimum area for this room shall be 100 square feet.

8. There shall be a lounge for staff use. Separate or combined lounges for male and female staff shall be provided. The lounge shall be designed to minimize the need to leave the suite and to ensure convenient access to the recovery room.

9. There shall be areas for dictation and report preparation which shall be accessible from the lounge area.

10. There shall be a janitor closet in both the sterile and non-sterile areas. Each shall contain a floor receptor or service sink and storage for janitorial supplies and equipment.

11. There shall be staff toilets.

12. There shall be a medication storage and distribution room which shall include a hand washing facility and a refrigerator.

13. If the outpatient surgery unit is located in a separate building or on a different campus, there shall be toilets for the handicapped.

(10) Obstetrical Facilities.

(a) At the option of the hospital, obstetrical suites may consist of any combination of the following major elements except that a Cesarean section/delivery room shall be provided in each facility. The requirement for a Cesarean section/delivery room will be waived for hospitals with 1,500 or fewer births per year. If the number of births exceeds 1,500 per year for 2 consecutive years, this requirement will no longer be subject to waiver and a Cesarean section/delivery room, recovery room and service areas as described shall be provided.

1. Cesarean Section/Delivery Room.

a. Each room shall have a minimum net usable clear area of 300 square feet with a minimum dimension of 15 feet.

b. Room temperature shall be individually controlled.

c. An area of the room shall be designated for infant resuscitation. There shall be a minimum of one oxygen, vacuum, medical air outlet and one critical power duplex receptacle in the resuscitation area.

d. There shall be two scrub sinks at the entrance to the Cesarean section/delivery room which shall be located to allow the physician to observe the patient while scrubbing.

2. Recovery Room.

a. Each recovery room shall contain a minimum of two beds and have a nurse position with charting facilities located to permit visual control of all beds. Each room shall include facilities for medicine administration and hand washing, a flushing rim clinical service sink with a bedpan flushing device, and cabinets for storage of equipment and supplies.

3. Service Area.

a. There shall be a control or nurse station located to permit observation of all traffic entering the obstetrical department.

b. There shall be an office for the obstetrical department director’s office which shall be located to allow visitors to the suite to confer with the director without passing through the suite or the sterile quarters.

c. There shall be a minimum of one high-speed sterilizer conveniently located to serve all delivery rooms.

d. At Cesarean section/delivery rooms, there shall be separate clothing change areas for male and female staff. These areas shall contain lockers, showers, toilets, urinals, lavatories equipped for hand washing, and space for changing into scrub attire. They shall be arranged to require a one-way traffic pattern so that personnel entering from outside the obstetrical suite can shower, change and move directly into the sterile corridor of the obstetrical suite.

e. There shall be a medication room with a work counter and sink.

f. There shall be an anesthesia storage and workroom which shall contain a work counter with a double compartment sink and storage cabinets.

g. There shall be a clean workroom with an area in the room for exchange carts. The room shall contain a work counter with sink and storage shelves.

h. There shall be an equipment cleanup and soiled workroom. This room shall include an area for carts and a work counter with a double compartment sink. There shall be a clinical service sink with a rinsing device.

i. There shall be an equipment storage room in a convenient location. The minimum size shall be 1 percent of the gross area of the department or 100 square feet, whichever is larger.

j. There shall be a family room near the entrance to the unit. Toilet facilities for the handicapped shall be adjacent to this room.

k. There shall be a janitor closet containing a floor receptor or service sink and storage for janitorial supplies and equipment for the exclusive use of the obstetrical suite.

l. There shall be a lounge and toilet facilities for obstetrical staff which is conveniently located to the labor, delivery and recovery areas.

m. There shall be private on-call bedrooms with toilets for physicians.

n. There shall be an area for storing stretchers which is out of the path of normal traffic.

o. There shall be a nourishment room with counter, sink and refrigerator.

p. If Labor-Delivery-Recovery (LDR) or Labor-Delivery-Recovery-Postpartum (LDRP) rooms are not provided, labor rooms complying with the following shall be provided.

(I) Each room shall be designed for either one or two beds with a minimum area of 100 square feet per bed. Two labor beds shall be provided for each delivery room.

(II) In facilities having only one delivery room, two separate labor rooms shall be provided, one of which shall be a minimum of 160 square feet and shall be equipped with a minimum of two oxygen outlets and two suction outlets in order to perform as an emergency delivery room.

(III) Each labor room shall contain a lavatory equipped for hand washing and shall have access to a toilet room. One toilet room may serve two labor rooms.

(IV) Labor rooms shall have controlled access with doors arranged for observation from a nurse work station.

(V) There shall be at least one shower for the use of patients in labor. A water closet shall be conveniently accessible to each shower facility.

4. Labor-Delivery-Recovery Room (LDR).

a. LDR rooms shall contain a minimum area of 250 square feet with a minimum dimension of 12 feet. This includes the toilet and shower room and concealable equipment storage area. Without a change in room area, the equipment may be kept in an additional storage room near the nurse station in lieu of a concealable storage area.

b. An infant resuscitation area shall be provided. This area shall be provided with a minimum of one oxygen, vacuum and medical air outlet. One duplex receptacle shall be connected to the critical branch and one duplex receptacle shall be connected to the normal branch.

c. The following shall be provided in the delivery area:

(I) One oxygen and one vacuum outlet;

(II) Four duplex receptacles connected to the critical branch and two duplex receptacles connected to the normal branch;

(III) Examination light controls;

(IV) A telephone or a communication system;

(V) A hand washing facility; and

(VI) Room light intensity controls.

d. Each LDR room shall have direct and exclusive access to a toilet and shower without going through the general corridor. All finishes in the room shall be selected for ease in cleaning as well as for contributing to a homelike atmosphere. The LDR room shall be located within the obstetrical department.

e. The service area requirements for normal patient rooms shall be provided for the LDR suite.

5. Labor-Delivery-Recovery-Postpartum Rooms (LDRP) shall meet all of the requirements of the labor-delivery-recovery suite. Additionally, each patient room shall have a window to the exterior. The window shall comply with all of the size, location and operational requirements of other patient room windows. Windows shall be appropriately curtained.

6. Holding Nursery.

a. In facilities that provide only LDR rooms with postpartum bedrooms or LDRP rooms, a full-term or Level I nursery is not required. In that case, a holding nursery shall be provided.

b. The holding nursery shall be sized at a ratio of one bassinet for every two and one-half postpartum beds.

c. Each bassinet position shall have 24 square feet of floor area.

d. There shall be a hand washing facility at a ratio of one for every six bassinets in each nursery.

e. Locate the nursery next to the nurse station and provide view windows to allow staff viewing.

(11) Emergency Service Department. When 24-hour emergency service is to be provided, the following elements shall be required.

(a) There shall be a grade level entrance sheltered from the weather. The entrance and driveway shall have direct access from the public roads for ambulance and vehicle traffic and shall be clearly marked. If a raised platform is used for ambulance discharge, a separate entrance for pedestrians and the handicapped shall be provided. There shall be an emergency access area to permit discharge of patients from automobiles and ambulances at the sheltered entrance. There shall be an area for temporary parking of such vehicles away from the entrance.

(b) There shall be a reception and control station located so as to permit staff to observe and control the access to treatment areas, pedestrian and ambulance entrances and the public waiting area.

(c) There shall be convenient wheelchair and stretcher storage. Such storage shall be out of the flow of traffic but with convenient access to emergency entrances.

(d) There shall be a public waiting area with adjacent toilet facilities, drinking fountains and telephones.

(e) There shall be a treatment and examination room which shall have a minimum of 100 square feet of clear floor space and shall contain a work counter with storage cabinets, hand washing facilities and an examination light. The number of treatment or examination rooms is dependent on the anticipated workload. These treatment areas may be in a large room with cubicle curtains providing privacy. In each such case, a minimum of one fully enclosed treatment or examination room shall be provided.

(f) There shall be an x-ray film illuminator which shall be conveniently located in the department.

(g) Provisions for orthopedic and cast work may be in a separate room. Located conveniently to the orthopedic work area, facilities shall be provided for storing splints and other orthopedic supplies, a plaster sink, an x-ray film illuminator and an examination light.

(h) A poison control center may be part of the nurse station.

(i) There shall be a shower near the entrance for the emergency wash-down of patients. The arrangement shall permit staff assistance.

(j) There shall be a soiled workroom. This room shall contain a flushing rim clinical service sink, a work counter with a double compartment sink. Receptacles for the disposal of soiled items shall also be included. If the room is to function as a soiled holding room, the work counter and double compartment sink may be eliminated, but a hand washing facility must be provided.

(k) There shall be a clean workroom equipped with a work counter and storage for medical supplies and a lavatory or sink for hand washing. If a clean holding room is provided, the requirements for fixed storage and hand washing are eliminated.

(l) There shall be a storage area for crash carts. Portable x-ray units and other equipment shall be located out of traffic and clearly accessible to each operating and treatment room.

(m) The hospital corridor system shall not pass directly through this unit.

(n) There shall be a station for staff work and charting with counters, cabinets and medication storage. This area may be combined with or include centers for reception control, poison control, after hours admitting and communication. There shall be convenient access to the hand washing facilities.

(o) There shall be locked cabinets or other secure storage for staff's personal effects within the nurses' work area or lounge.

(p) There shall be staff toilets.

(q) There shall be a janitor closet for the exclusive use of the emergency department. This must be located within or adjacent to the emergency service area.

(r) For electrical design purposes only, trauma rooms shall be synonymous with treatment rooms.

(12) Radiology Suite.

(a) Each hospital shall provide facilities for diagnostic radiographic examination of patients. The number of radiographic and fluoroscopic rooms is dependent on the anticipated workload and shall contain the following features.

(b) Radiographic and fluoroscopic functions may be performed in one room or in separate rooms. The room shall be appropriately sized to accommodate equipment, patient stretchers and staff work area. Shielded control areas shall be included in or adjacent to each radiographic room with provisions for viewing the entire table and patient and for audio communication during film exposure. See the licensing and registration requirements in Chapter 10D-56, F.A.C.

1. Each fluoroscopic room shall have an adjacent patient toilet room. This patient toilet room shall contain a water closet and a hand washing facility. One door must open out from the toilet room.

2. A barium preparation area shall be provided with sink, work counter and storage area to allow mixing of contrast media. One barium preparation unit may serve several radiographic rooms. Premixed commercial preparations, if used, may be stored in a conveniently located clean workroom.

3. A cleanup facility shall be provided within the suite and shall include a service sink and storage space for equipment and supplies.

4. An alcove shall be provided near the processor for viewing film immediately after it is processed.

5. There shall be offices for the radiologists and other staff as required. There shall be facilities for the storage of active x-ray film conveniently located for immediate film retrieval.

6. There shall be a film storage room for inactive records. The room may be outside the radiology suite but must be under the administrative control of the radiology department with provisions to secure films against loss or damage.

7. There shall be the necessary clerical offices.

8. There shall be a patient stretcher holding alcove adjacent to each radiographic area.

9. There shall be a hand washing facility in each procedure room. Hand washing facilities may be omitted from rooms used only for routine screening such as chest x-rays.

10. There shall be a toilet room with hand washing facilities conveniently located to waiting areas. The toilet room shall be usable and accessible for wheelchair patients. Separate toilets shall be provided with direct access to each radiographic room routinely used for fluoroscopic procedures and arranged so that a patient may leave the toilet room without reentering the fluoroscopic area.

11. There shall be staff toilets.

12. There shall be patient dressing rooms conveniently located to the waiting area and to the radiographic rooms. Dressing rooms shall include a seat or bench, a mirror and provisions for hanging the patient’s clothing. At least one dressing room in the radiographic suite shall be sized for access and use by wheelchair patients.

(13) Laboratory Suite.

(a) Each hospital shall provide laboratory facilities for hematology, clinical chemistry, urinalysis, microbiology, serology, anatomic pathology and a transfusion service to meet the workload anticipated by the hospital. At a minimum, the laboratory shall provide for the following procedures to be performed on site:

1. Blood count;

2. Urinalysis;

3. Blood glucose, electrolytes, blood urea and nitrogen (BUN), amylase; and

4. Transfusion type and cross match capacity.

(b) At a minimum, the laboratory suite shall contain the following.

1. There shall be a laboratory work counter with space for microscopes, appropriate chemical analyzers, incubators and centrifuge. Work areas shall include access to vacuum, gas and electrical services, as needed, and sinks with water.

2. There shall be refrigerated facilities for the storage of blood for transfusions. The blood storage refrigerator shall be equipped with temperature monitoring and alarm signaling devices.

3. There shall be lavatories or counter sinks equipped for hand washing. These counter sinks may be used for the disposal of nontoxic fluids.

4. There shall be storage facilities for reagents, standards, supplies and stained specimens, microscope slides, etc., including refrigeration as needed. There shall be separate, well ventilated storage facilities for volatile liquids.

5. There shall be separate rooms for bacteriology and histology. The minimum size for each room shall be 80 square feet.

6. If outpatient services are provided, a specimen blood, urine and feces collection facility shall be required. The blood collection area shall have work counter space and hand washing facilities. The urine and fecal collection room shall be equipped with a water closet with a rinsing device and a lavatory.

7. There shall be emergency shower and eye flushing devices and fire blankets.

8. If radioactive materials are employed, there shall be facilities for long-term storage and disposal of these materials. No special provisions will be required for body waste products for patients receiving low level isotope diagnostic material.

9. There shall be administrative areas including offices and space for clerical work, filing and records maintenance.

10. There shall be lounge, locker and toilet facilities which shall be conveniently located for male and female laboratory staff. These may be outside the laboratory area and shared with other departments.

(c) Licensure for this laboratory facility shall be required in accordance with Chapter 483, F.S., and as prescribed in Chapter 59A-7, F.A.C.

(14) Rehabilitation Therapy Department.

(a) If formal rehabilitative therapy services are included as part of the services rendered by the hospital such as physical therapy, occupational therapy or respiratory therapy, all of the requirements of this section shall be met. Where two or more rehabilitative services are included, some of the requirements may be shared as appropriate.

(b) Each rehabilitative therapy department shall include the following common elements which may be shared or provided as separate units for each service.

1. There shall be an office and clerical space for filing and retrieving patient records.

2. There shall be a reception and control station with visual control of the waiting and activities areas. This may be combined with the office and clerical space.

3. There shall be outpatient waiting areas which are out of the general traffic.

4. There shall be patient toilets with hand washing facilities accessible to the handicapped.

5. There shall be storage space or spaces for parking wheelchairs and stretchers out of traffic while patients are using the services. These spaces may be separate from the service area but must be located for convenient use.

(c) Physical Therapy. If physical therapy is part of the service, at a minimum, the following shall be included.

1. There shall be individual treatment areas which shall have a minimum of 60 square feet of clear floor area.

2. There shall be hand washing facilities either within or at each treatment area for staff use. One hand washing facility may serve a maximum of three treatment areas.

3. There shall be an exercise area and facilities.

4. There shall be storage for clean linen and towels. This may be in cabinets, closets or in carts located for convenient use and out of traffic.

5. There shall be storage for equipment and supplies.

6. There shall be separate storage for soiled linen, towels and supplies.

7. There shall be a patient toilet room with a hand washing facility.

(d) Occupational Therapy. If occupational therapy services are provided, the following shall be included.

1. There shall be work areas and counters suitable for wheelchair access.

2. There shall be hand washing facilities.

3. There shall be storage for supplies and equipment.

(e) Respiratory Therapy Services.

1. If respiratory therapy services are provided, the following requirements shall be met.

a. There shall be storage for supplies and equipment.

b. There shall be space and utilities for cleaning and sanitizing equipment.

c. There shall be service facilities for calibrating, adjusting, servicing and minor repairing of equipment.

2. Respiratory therapy services shall be conveniently accessible on a 24-hour basis to the intensive care units.

3. If respiratory therapy services such as testing and demonstration for outpatients are part of the hospital’s services, additional facilities and equipment shall be provided as necessary.

(15) Morgue and Autopsy.

(a) Morgue and autopsy facilities shall be accessible to the exterior entrance and shall be located so as to avoid the need for transporting bodies through public areas.

(b) At a minimum, the following facilities shall be provided when autopsies are performed within the hospital.

1. There shall be refrigerated body holding facilities.

2. There shall be an autopsy room. This room shall contain an autopsy table and a work counter with a sink equipped for hand washing.

3. There shall be storage space for supplies, equipment and specimens.

4. There shall be a clothing change area equipped with shower, toilet and lockers.

5. There shall be a janitor closet with floor receptor or sink and facilities for storing janitorial equipment and supplies.

(c) If autopsies are performed outside the facility, only a well ventilated body holding room shall be required.

(16) Pharmacy.

(a) A pharmacy shall be provided in the hospital. The facilities and equipment necessary shall be adequate to handle the pharmacy and medicine requirements of the hospital.

(b) The pharmacy shall include the following.

1. There shall be a pick-up and receiving counter, an area for reviewing and recording orders, an extemporaneous compounding area, work counters and cabinets for pharmaceutical activities and an area for temporary storage, exchange and restocking of carts.

2. There shall be a compounding area.

3. There shall be space for packaging, labeling and quality control.

4. There shall be space for bulk, active and refrigerated storage. Special care shall be taken in storing bulk quantities and alcohol. There shall be secure storage for controlled substances. There shall be separate storage for general supplies and equipment when not in use.

5. There shall be separate administrative space for office functions including filing, communication and reference. This is not required in psychiatric hospitals.

6. There shall be hand washing facilities within each room where open medication is handled.

7. If a unit dose procedure is used, there shall be additional space and equipment for supplies, packaging, labeling and for storing the carts.

8. If intravenous solutions are prepared in the pharmacy, there shall be an area for a laminar flow bench and hood. The laminar flow system shall include a non-hygroscopic filter rated at 99.97 percent efficiency, HEPA, per DOP test. A visible pressure gauge shall be provided which measures the pressure drop across the filter.

(17) Dietary Facilities.

(a) Food service facilities and equipment shall be provided as needed to meet the dietary requirements of the hospital. A conventional or convenience food preparation system or any appropriate combination thereof is acceptable.

(b) The following facilities shall be provided in the size required to meet the needs and to implement the type of food service selected.

1. There shall be a control station for receiving and controlling food supplies.

2. There shall be storage, including cold storage space.

3. There shall be food preparation facilities.

4. There shall be hand washing facilities.

5. There shall be facilities for assembling and distributing patient meals. This is not required in psychiatric facilities.

6. There shall be a dining room for ambulatory patients, staff and visitors.

7. There shall be facilities for ware washing located in a room or an alcove that is separate from the food preparation area. Commercial type ware washing equipment shall be provided. There shall be separation between the receiving, scraping, sorting and stacking of soiled tableware and the clean tableware collecting area. Hand washing facilities shall be conveniently available in the soiled tableware side.

8. There shall be facilities for pot washing.

9. There shall be a storage area and sanitizing facilities for cans, carts and mobile tray conveyors.

10. There shall be facilities for waste storage which are located in a separate room easily accessible to the outside for direct pick up or disposal.

11. There shall be an office for the dietary service manager with additional space or a separate office provided for the dietitian.

12. There shall be toilets with hand washing facilities within the dietary department. Such toilets shall have a separate vestibule.

13. There shall be a janitor closet within the dietary department which shall include a floor receptor and storage space for janitorial supplies and equipment.

14. There shall be ice making equipment either within the food preparation area or in a separate room.

(18) Administration and Public Areas.

(a) All public waiting areas shall be provided with male and female toilets designed to accommodate the handicapped. Such facilities shall be within 75 feet of the waiting area and may serve more than one such area.

(b) The entrance shall be at grade level and shall be sheltered from inclement weather and accessible to the handicapped.

(c) A lobby shall be provided which includes a counter or desk for reception and information, public waiting areas, public telephones and drinking fountains.

(d) Interview space shall be provided which allows for private interviews relating to social services, credit and admissions.

(e) There shall be an admissions area with a separate waiting area for patients and accompanying persons. This area shall include a work counter or desk for staff and a storage area for wheelchairs which is out of the path of normal traffic.

(f) There shall be general business offices for hospital business transactions, medical and financial records and offices for the administrative and professional staff.

(g) There shall be a minimum of one multipurpose room for conferences, meetings and health education purposes, including provisions for using visual aids.

(h) There shall be a medical library. The library may be an area within the physicians' lounge or the medical records department.

(i) There shall be space for storing office equipment and supplies.

(19) Mobile Testing and Treatment Facilities.

(a) There shall be sturdy walls, fences or bollards around the immediate site to prevent collisions with the unit by other vehicles.

(b) Electrical connection to the hospital electrical system shall be permitted only when the mobile facility complies with appropriate requirements of NFPA-70, National Electrical Code.

(c) There shall be a rain-free passage from the hospital to the entrance to the mobile facility.

(d) A fire alarm system shall be provided. An alarm initiated in the mobile facility shall activate the hospital system, and an in-house alarm shall sound an alarm in the facility.

(e) The mobile facility shall not diminish egress from the hospital.

(f) Mobile facilities shall be approved in advance by the Office of Plans and Construction and the Office of Licensure and Certification.

(g) Egress from the mobile facility shall conform with health care occupancy standards of the Life Safety Code.

(h) There shall be a telephone which shall be connected to the hospital communication system.

(20) Medical Records. There shall be rooms, areas and offices for the medical records administrator or technician for purposes of review and dictation, for sorting, recording and microfilming records and for records storage.

(21) Central Sterile Supply Services. Each hospital, except psychiatric hospitals, shall provide a central sterile supply services department comprised of the following elements.

(a) There shall be a receiving and decontamination room. At a minimum, this room shall contain work space and equipment for cleaning medical and surgical equipment and for disposing of used and soiled material. This room shall include facilities for hand washing.

(b) There shall be a clean workroom which shall contain facilities for hand washing and work space and equipment for terminal sterilization and sanitation of medical and surgical equipment and supplies.

(c) There shall be a storage area for clean medical, surgical supplies and for sterile supplies. This area may be part of the clean workroom.

(d) There shall be a room for storage of equipment used in the delivery of patient care.

(22) General Storage.

(a) There shall be a general storage facility with a minimum total area of 20 square feet per inpatient bed. In psychiatric and rehabilitation hospitals, general storage shall be provided with a minimum total area of 5 square feet per inpatient bed.

1. There shall be receiving areas.

2. There shall be off-street unloading facilities.

(b) If the general storage areas are located in a separate building on the site, provisions shall be made for protecting supplies against inclement weather during transfer. At a minimum, a covered walkway may be used for this purpose. The off-street loading facilities and receiving areas for the general stores shall not be part of the general means of egress for the building.

(23) Linen Services.

(a) Each hospital shall have provisions for storing and processing clean and soiled linens as required for appropriate patient care. Processing may be done within the facility in a separate building on or off site, or in a commercial or shared laundry.

(b) At a minimum, the following facilities shall be included.

1. There shall be a separate room for receiving and holding soiled linen until it is ready for pickup or processing.

2. There shall be a central storage room issuing clean linen. The central storage capacity shall be sufficient for four day’s operation or two normal deliveries, whichever is greater.

3. There shall be a cart storage area for separate out-of-traffic parking of clean and soiled linen carts.

4. There shall be a clean linen inspection and mending room or area.

5. Hand washing facilities shall be provided in each area where unbagged soiled linen is handled.

6. If linen is processed outside the building, provisions shall be made for a service entrance which is protected from inclement weather during loading and unloading of linen.

7. If linen is processed in a laundry facility which is part of the hospital, the following shall be provided.

a. There shall be a receiving, holding and sorting room for the control and distribution of soiled linen. Discharge from soiled linen chutes may occur within this room or into a separate room.

b. There shall be a laundry processing room. The equipment shall be arranged so as to permit an orderly flow with minimum cross traffic that would mix clean and soiled operations.

c. There shall be a storage area for laundry supplies.

d. There shall be hand washing facilities for employees in each separate room where clean or soiled linen is processed and handled.

(24) Employee Facilities. Lockers, lounges and toilets shall be provided for employees and volunteers. These shall be in addition to and separate from those required for the medical staff and the public.

(25) Janitor Closets. In addition to the janitor closets specifically required in certain departments, sufficient janitor closets shall be provided throughout the facility as required to maintain a clean and sanitary environment. Each janitor closet shall contain a floor receptor or service sink and storage space for janitorial equipment and supplies. There shall be a minimum of one janitor closet on each floor.

(26) Engineering Service and Equipment Areas.

(a) There shall be a room or separate building for boilers, fire pumps, and mechanical and electrical equipment.

(b) There shall be an office for the building engineer with file space and provision for the protected storage of the facility’s drawings, records and manuals.

(c) There shall be a general maintenance shop for repair and maintenance with a separate area for building maintenance supplies. Special care shall be taken in designing and constructing spaces used for storing solvents and flammable liquids to ensure conformance with applicable NFPA codes. This is also required for the carpentry shops and other dust producing areas.

(d) There shall be a separate area or room specifically for storing, repairing and testing electronic and other medical equipment. This is not required in psychiatric hospitals.

(e) A storage room shall be provided for yard equipment which is located so that the equipment may be moved directly to the exterior.

(27) Waste Processing Services. Facilities shall be provided for the sanitary storage and disposal of waste by incineration, mechanical destruction, compacting, containerization removal, or sterilization or by a combination of these techniques. Biohazardous waste disposal shall comply with the requirements contained in Chapter 64E-16, F.A.C.

(28) There shall be public toilet rooms on each floor which are designed to accommodate the handicapped.

(29) Rehabilitation Hospitals. New rehabilitation hospitals shall be required to meet all of the requirements as stated in Rule 59A-3.081, F.A.C. for general hospitals except as modified herein.

(a) Surgical, and obstetrical and emergency room facilities are not required.

(b) In hospitals with a bed capacity of 200 or less, the requirements for diagnostic radiology and laboratory are not required if outside contractual arrangements are made to provide these services.

(c) Physical Therapy Unit.

1. There shall be an office for the physical therapist.

2. There shall be waiting areas.

3. There shall be facilities for hand washing. These facilities may serve more than one cubicle.

4. There shall be a group exercise area.

5. There shall be a room for storing linen supplies and equipment.

6. There shall be patient dressing areas with shower, lockers and toilet rooms.

7. There shall be a janitor closet with floor receptor.

(30) Psychiatric Hospitals. New psychiatric hospitals and new psychiatric sections in general hospitals shall comply with all of the minimum standards set forth in subsections 59A-3.081(1) through (28), F.A.C. for general hospitals except for the requirements for isolation facilities and surgical and obstetrical services. Diagnostic x-rays and laboratory services may be provided by contract if such services are available locally.

(a) Each patient sleeping room intended for occupancy for 24 hours or longer shall have an outside window or outside door arranged and located so that it can be opened from the inside to permit venting products of combustion and to provide fresh air to any occupant in case of emergency.

(b) In buildings housing high risk of patients or having detention rooms or security sections, it will be necessary to provide detention screens or polycarbonate glazing to confine and protect building inhabitants.

1. Where windows require the use of tools and keys for operation because of detention screens, the tools or keys shall be located on the floor or area involved at a prominent location which is accessible to staff.

2. Where glass fragments may create a hazard, safety glazing and other appropriate security features shall be incorporated.

3. The degree of security required in the window opening to inhibit the possible tendency for suicide or escape shall be determined by the hospital.

(c) A nurse call system is not required; however, a voice activated and switchable emergency calling system shall be provided in seclusion rooms. If a nurse call system is included, provisions shall be made to permit the removal of call buttons or for the use of blank plates as required for security.

(d) Each patient shall have access to a toilet room without entering the general corridor area.

1. One toilet room shall serve no more than four beds and no more than two patient rooms.

2. The lavatory may be in either the patient bedroom or in the toilet room. A tub or shower may be added to the toilet room as required by the hospital. All mirrors shall be non-breakable.

3. Psychiatric services for children which require the observation and control of patient activity may vary from these requirements.

(e) The service areas shall be located in or readily available to each nursing unit. Each service area may be arranged and located to serve more than one nursing unit, but a minimum of one such service area shall be provided on each nursing floor.

1. There shall be an administrative center or nurse station.

2. There shall be a staff lounge and/or a conference room.

3. There shall be facilities for hand washing which are located near the nurse station and the drug distribution station. One lavatory may serve both areas.

4. A charting area shall be provided with adequate space for the function. There shall be acoustical privacy.

5. A viewing window to permit observation of the patient area by the charting nurse or physician may be used if it is located so that the patient files cannot be read from outside the charting space.

6. A minimum of two separate social areas shall be provided, one appropriate for noisy activities and the other for quiet activities. The combined total area shall be a minimum of 40 square feet per bed space or a minimum of 160 square feet for each of the two areas, whichever is greater. The noisy activity areas may be combined and may be remotely located.

7. There shall be a room for group therapy. The area of the room shall be a minimum of 250 square feet. The group therapy room may be combined with the area for quiet activities, provided the total area is a minimum of 400 square feet if used for both functions.

8. Patient laundry facilities with automatic washers and dryers may be provided.

9. Separate consultation rooms, each with a minimum floor space of 100 square feet, shall be provided at a rate of one consultation room for the first 24 beds or any portion thereof. For each additional 24 beds or any portion thereof, there shall be one additional consultation room. The rooms shall be arranged for acoustical and visual privacy.

10. Space for occupational therapy shall be provided with a minimum area of 375 square feet or at a rate of 4 square feet per bed, whichever is greater. This space shall include provisions for hand washing, work counters, storage and displays.

11. Where psychiatric facilities contain fewer than 25 beds, the occupational therapy function may be performed within the noisy activities area if a minimum space of 495 square feet is available for both the noisy activity area and the occupational therapy activities. If the occupational therapy function is performed within the noisy activities area, that space shall contain provisions for hand washing, work counters, storage and displays.

12. There shall be a lounge and toilet rooms for staff.

13. There shall be individual closets or compartments for the safekeeping of personal belongings of the nursing personnel. These shall be located so as to be convenient to the duty station of the personnel or in a central location.

14. There shall be space for examination and treatment of patients which shall contain a minimum floor area of 120 square feet excluding space for vestibules, toilet and closets. The minimum room dimension shall be 10 feet. The room shall contain a lavatory or sink equipped for hand washing, a work counter, storage facilities and a desk counter or shelf space for writing. The emergency treatment room may be used for this purpose if it is conveniently located on the same floor as the patient rooms.

(f) There shall be a clean linen area for the storage and distribution of clean linen. The required area may be concentrated in one central room or divided into several rooms throughout the facility.

(g) There shall be a soiled linen area. The area shall be part of the system for collecting and disposing of soiled materials and shall include a holding room for soiled linens. The required area may be concentrated in one room or divided into several rooms throughout the facility. There shall be a lavatory for hand washing in each soiled linen area.

(h) There shall be a drug distribution station which shall contain a minimum area of 30 square feet. Provisions shall be made for convenient and prompt 24-hour distribution of medicine to patients. This may be from a medicine preparation room or from a self-contained medicine dispensing unit. The area may be located at the nurse station and shall be under the visual control of the nursing staff. It shall contain a work counter and sink, a refrigerator and locked storage for biologicals and drugs. The drug distribution station shall be under the direct control of the nursing or pharmacy staff, and provisions for security against unauthorized access must be assured.

(i) There shall be a small kitchen for patient use.

(j) There shall be patient bathing facilities. Bathtubs or showers shall be provided at a rate of one for every four bed spaces which are not otherwise served by bathing facilities within the patients' rooms. Each tub or shower shall be in an individual room or enclosure which provides space for the private use of the bathing fixture and for drying and dressing.

(k) There shall be space for storing emergency equipment which shall be under the direct control of the nursing staff and in close proximity to the nurse station and out of traffic.

(l) There shall be a seclusion room for patients requiring security and protection from either themselves or others. The room area shall be a minimum of 60 square feet and the room dimension shall be a minimum of 6 feet.

1. The room shall be located and designed in such a manner as to afford direct supervision and observation of the patient and the entire room by the nursing staff. It shall be a single room and shall be constructed to minimize the patient’s hiding, escape, injury or suicide. Rooms may be grouped together or placed in every psychiatric nursing unit.

2. The seclusion room is intended for short-term occupancy by patients who become violent or may be suicidal; therefore, special fixtures, hardware, and tamper-proof screws shall be used. Doors shall open out and shall have provision for staff observation while maintaining privacy from the public and other patients. The seclusion room shall have natural light–skylight, window or small thick glass opening to the exterior–to maintain a therapeutic environment.

(m) In facilities designed for geriatric psychiatric patients, there shall be soiled workrooms which comply with the requirements for medical-surgical beds.

(n) Multi-storied psychiatric hospitals shall have elevators.

1. In multi-storied facilities, a minimum of one elevator shall be provided which is hospital size with 4,000 pound capacity. The other elevators may be normal passenger elevators with 2,500 pound capacity. If appropriately located, a freight elevator may be substituted for the hospital size elevator.

2. The quantity of elevators shall be as required by paragraphs 59A-3.081(37)(a) through (e), F.A.C.

(o) Televisions in psychiatric patient rooms are optional. Where televisions are not provided, associated electrical services may likewise be omitted.

(31) Details and Finishes. The following describes the requirements for details and finishes in new hospitals and for additions, alterations and renovations to existing hospitals.

(a) Corridors in patient care and treatment areas must be a minimum of 8 feet in clear and unobstructed width except in psychiatric facilities where 6-foot corridors are acceptable. In psychiatric facilities housing geriatric patients, corridors in patient care and treatment areas must be a minimum of 8 feet in clear and unobstructed width. Equipment such as drinking fountains, telephone booths and time clocks shall be located in alcoves or in other locations so as not to infringe on the corridor space and not reduce the corridor width below the required minimum. Corridors in non-patient care areas shall be a minimum of 44 inches in clear width.

(b) Smaller rooms which may be occupied by patients and which contain bathtubs, sitz baths, showers and water closets shall have doors which open away from the room. When such rooms are necessarily on corridors, the corridors shall be equipped with alcoves to accommodate the door swinging outward. These alcoves must be designed to allow a minimum of 1 foot from the latch side of the door frame to allow opening by persons in wheelchairs. In non-corridor locations where doors opening outward are not feasible, the door and frame shall be fitted with rescue-type hardware.

(c) Doors to patient sleeping rooms, treatment rooms, examination rooms and exits shall be a minimum of 44 inches wide and a minimum of 80 inches high. Doors to other rooms and spaces shall be a minimum of 34 inches wide. In patient areas of rehabilitation hospitals, there shall be a minimum clearance of 1 foot at the strike side of the door to accommodate wheelchair accessibility. Patient room doors in psychiatric hospitals shall be a minimum of 36 inches wide except doors to patient rooms in geriatric psychiatric areas shall be a minimum width of 44 inches.

(d) Doors shall not swing into corridors except those in spaces that are not subject to occupancy such as small closets. Large walk-in closets are considered occupiable spaces.

(e) Patient charting desks that fold down from the wall are not permitted to intrude on the required corridor space, and if used, must be placed in an alcove of sufficient depth to eliminate any intrusion on the corridor space.

(f) Patient sleeping rooms shall be provided with operable windows to the exterior sized to equal at least 8 percent of the gross floor area of the room. All windows shall have a minimum 20-foot unobstructed vista. This vista is measured perpendicularly from the plane of the window. Other than in intensive care units, the maximum stool height in patient sleeping rooms may not exceed 3 feet above the finished floor. Window locking and operating mechanisms may not be more than 72 inches above the finished floor. Window stools in intensive care units may not exceed 5 feet above the finished floor.

(g) Flat plates, if used as sills under A-labeled doors and expansion joint covers, shall be flush with the adjacent finished floor covering and the surface shall be smooth.

(h) Ceiling heights shall be as follows.

1. Ceilings in rooms with ceiling-mounted surgical light fixtures and in kitchens shall be a minimum height of 9 feet.

2. In psychiatric facilities, ceilings in patient bedrooms and seclusion rooms shall be a minimum height of 9 feet.

3. Ceilings in corridors and patient toilet room shall be a minimum height of 7 feet 6 inches. Lighting fixtures, signs and other equipment shall not extend below a height of 6 feet 8 inches above the finished floor. Ceilings in all other rooms shall be a minimum height of 8 feet.

4. When remodeling existing facilities, written approval by the Office of Plans and Construction shall be required in advance for ceiling heights which are lower than the above minimums.

(i) Ceilings shall be acoustically treated in corridors in patient areas, nurse stations and dining rooms. Ceilings in kitchens, operating rooms and delivery rooms, including LDR and LDRP rooms, shall be washable.

(j) Dispensers for single-service paper towels and soap dispensers shall be provided at all hand washing facilities.

(k) The walls in patient treatment areas and sleeping areas shall be washable; and in the immediate area of plumbing fixtures, the finish shall be moisture resistant.

(l) Toilet compartment partitions and urinal screens in the men’s toilet rooms shall not be constructed of enameled steel.

(m) Wall bases in operating rooms and Cesarean section/delivery rooms shall be integral with the floor surface material and shall be without voids that can harbor harmful bacteria.

(n) All smoke partitions, horizontal exits and exit passageway partitions shall be constructed prior to the construction of intervening walls.

1. Smoke partitions shall be constructed so as to provide a continuous smoke-tight membrane from exterior wall to exterior wall and from the floor to the underside of the deck above. This includes interstitial space and the area above solid fire tested membranes.

2. Where it is not possible to inspect smoke partitions because of the fire tested membrane, fire-rated access panels shall be installed adjacent to each side of the smoke partitions at intervals not exceeding 30 feet and in such locations as necessary to view all surfaces of the partition.

3. No items shall be recessed in smoke partitions, horizontal exits and exit passageway walls which will compromise the fire integrity.

4. Where plaster or gypsum wallboard are used to construct such partitions, each side of the partition shall be continuous from outside wall to outside wall and from the floor to the underside of the deck above, interrupted only by doors and ventilation duct work which has been dampered properly to prevent the passage of smoke.

5. Where electrical conduits, cable trays, ducts and utility pipes pass through the smoke partitions, the utilities shall be located so that access is maintained to adjacent wall surfaces and to all damper access panels. The details shall show the studs and reinforcing half studs so that proper support is provided for the wall surfacing material. There shall be a minimum clearance of 6 inches between all conduits, piping and duct work at corridor walls to facilitate the inspection of these walls.

(o) The design and construction of linen and refuse chutes shall be in accordance with NFPA-82, Standard on Incinerators, Waste and Linen Handling Systems and Equipment as prescribed by Rule Chapter 4A-3, F.A.C.

1. Dumbwaiters, conveyors and other material handling systems shall not open directly into a corridor or exit way but shall open into a room enclosed by construction having a minimum fire resistance of 1 hour and provided with Class B-labeled, 1-hour fire-rated doors.

2. Service entry doors to vertical shafts containing dumbwaiters, conveyors and material handling systems shall be not less than Class B-labeled, 1 1/2-hour fire-rated doors. Material handling systems designed to open directly to the service area without the use of doors shall be fitted with tight closing smoke dampers. The doors of smoke dampers used in these systems shall close upon activation of a local smoke detector.

(p) In general hospitals and rehabilitation hospitals, and in those areas designed for handicapped people, grab bars shall be provided at patient use toilets, showers and tubs. The bars shall be 1 1/2 inches in diameter, shall have 1 1/2 inch clearance to walls and shall be of sufficient strength and anchorage to sustain a concentrated load of 250 pounds for 5 minutes. Fully recessed soap dishes shall be provided for all tubs and showers.

(q) Mirrors shall not be installed at hand washing facilities in food preparation areas and in clean utility rooms.

(32) Recreation rooms, exercise rooms and similar spaces where impact noises may be generated shall not be located directly over patient bed areas unless special provisions are made to minimize noise.

(33) Floor materials shall be easily cleanable and shall have wear resistance appropriate for the location involved. Floors in areas used for food preparation and food assembly shall be water resistant and grease proof. Joints in ceramic tile, quarry tile and similar materials in food preparation, food assembly, ware washing and other areas subject to harsh chemicals shall be of a material not affected by such chemicals. In all areas frequently subject to wet cleaning methods, floor materials shall not be physically affected by germicides and cleaning solutions. Floors that are subject to traffic while wet, such as assisted and non-assisted shower and bath areas, kitchens and similar work areas, shall have a nonslip surface.

(34) Wall bases in kitchens, toilets and other areas which are frequently subject to wet cleaning methods shall be made integral and cove with the floor, tightly sealed within the wall and constructed without voids that can harbor insects.

(35) The finished ceiling in the dietary and food preparation areas shall enclose all overhead duct work and piping.

(36) Finished ceilings may be omitted in mechanical and equipment spaces, repair workshops, general storage areas and similar spaces unless the ceiling is required for structural fire protection purposes.

(37) Elevators Where Required. All hospitals where either patient beds or a critical service facility such as operating, delivery, diagnostic, recreation, patient dining or therapy rooms are located on more than one floor shall have electric or electrohydraulic elevators and shall be in compliance with the requirements of Rule Chapter 4A-47, F.A.C., (Florida Elevator Safety Code) as follows:

(a) At least one hospital type elevator shall be installed where 1 to 59 patient beds are located on any floor other than the first floor. For purposes of these requirements, the first floor is that floor first reached from the main front entrance.

(b) At least two hospital type elevators shall be installed:

1. Where 60 to 200 patient beds are located on floors other than the first; or

2. Where service facilities are located on a floor other than that containing the patient beds.

(c) A minimum of three hospital type elevators shall be installed:

1. Where 201 to 350 patient beds are located on a floor other than the first floor;

2. Where service facilities are located on a floor other than the first; or

3. Where service facilities are located on a floor other than that containing the patient beds.

(d) For hospitals with more than 350 beds, the number of elevators shall be determined by an independent study of the hospital plan and the estimated vertical transportation requirements. In no case shall there be fewer than three elevators.

(e) Hospital type elevator cars shall have inside dimensions that will accommodate a standard patient bed and attendants. The car door shall have a minimum clear opening of 4 feet wide by 7 feet high. The minimum capacity of the elevator shall be 4,000 pounds. Additional elevators installed for visitors and material handling may be of a size less than noted above, but they shall be subject to the standards for access by the handicapped.

1. Leveling. Elevators shall be equipped with a 1-way automatic level maintaining device with an accuracy of + or - 1/4 inch.

2. Operation. Except those dedicated for material handling, each elevator shall be equipped with a two-way special service switch for staff use to permit cars to bypass all landing button calls and be dispatched directly to any floor. The fireman’s service function may be used.

3. Elevator controls, landing calls, alarm buttons and telephones shall be accessible to wheelchair occupants.

4. Elevator call buttons and controls shall be of the type that will not be activated by heat or smoke. If used for operation of door reopening devices without physical contact, light beams shall be provided in addition to door edge safety devices. The light beams shall be interconnected with a system of smoke detectors so that in case of smoke at any landing, the light control feature will be overridden or disengaged.

(38) Water Supply and Sewage Disposal.

(a) Water Supply. An approved, accessible, adequate, safe and potable supply of water shall be available at all times for drinking, culinary, bathing, cleaning and laundry purposes. Hot water shall be supplied to all lavatory and sink plumbing fixtures available for use by patients and staff.

(b) Sewage Disposal. An approved, adequate and safe method of sewage collection, treatment and disposal shall be provided for each hospital.

(39) Heating, Ventilating and Air Conditioning Systems. Air handling equipment shall be located in mechanical equipment rooms unless it serves only one room and is located in that room.

(a) Ventilation. Ventilation shall be provided by mechanical means in all rooms in new facilities and in all remodeled rooms. The minimum quantities and filtrations shall be met as set forth in the Minimum Hospital Ventilation Rate Tables for those spaces that are listed. These requirements apply to inpatient areas and outpatient areas within the hospital. Detached outpatient facilities shall comply with subsection (3) below except that outpatient surgery, outpatient cardiac catheterization and any other treatment or diagnostic procedure involving invasive procedures shall comply with the requirements for patient areas within the hospital.

| MINIMUM HOSPITAL VENTILATION RATE TABLE (See Note 2) |
| --- |
| GENERAL ACUTE CARE HOSPITALS |
|  |  |  | Outdoor | 100% | System * |
| Room or | Relative | Total | Air | Exhaust | & |
| Function | Pressure | Air | Quantities | Quantities | Filtration** |
| Operating, |  |  |  |  |  |
| Emergency |  |  |  |  |  |
| Operating Rooms, |  |  |  |  |  |
| Cystology | + | 20 | 5 | NO | 1A, 2A |
| Delivery | + | 12 | 5 | NO | 1A, 2A |
| Recovery | 0 | 6 | 2 | NO | 1A, 2A |
| Nursery | + | 12 | 2.8 | NO | 1A, 2A |
| Intensive Care | + | 6 | 2 | NO | 1A, 2A |
| Patient | 0 | 4 | 1.5 | NO | 1A, 2B, 3D |
| Labor, LDR and | 0 | 4 | 1.5 | NO | 1A, 2B |
| LDRP Room |  |  |  |  |  |
| Magnetic Resonance | + | 6 | 2 | NO | 1A, 2B |
| Imaging, Lithotripter |  |  |  |  |  |
| Patient Area Corridor | 0 | 2 | 1.5 | NO | 1A, 2B |
| Immunosuppressant | + | 2 | 1 | NO | 1E |
| Patient Room |  |  |  |  |  |
| Patient Isolation | - | 6 | 2 | YES | 1A, 2B |
| Room Without |  |  |  |  |  |
| Anteroom |  |  |  |  |  |
| Patient Isolation | 0 | 6 | 2 | YES | 1A, 2B |
| Room With |  |  |  |  |  |
| Walk-Through |  |  |  |  |  |
| Anteroom as the |  |  |  |  |  |
| Only Entrance |  |  |  |  |  |
| Anteroom | - | 6 | 2 | YES | 1A, 2B |
| Endoscopy | 0 | 6 | 2 | NO | 1A, 2B |
|  |  |  | * |  |  |
| Exam and Treatment | 0 | 6 | 2 | NO | 1A, 2B |
| Nourishment Pantry | 0 | 6 | 1 | NO | 1A, 2B |
| Medicine Preparation | 0 | 6 | 1 | NO | 1A, 2B |
| Clean Workroom | + | 4 | 2 | NO | 1A, 2B |
| Soiled Workroom | - | 10 | 2 | YES | 1A, 2B |
| Therapy (Physical | - | 4 | 2.25 | NO | 1A, 2B |
| and Hydro) |  |  |  |  |  |
| Respiratory Therapy | + | 6 | 2.25 | NO | 1A, 2B |
| Radiology | 0 | 6 | 2 | NO | 1A, 2B |
| Fluoroscopic | - | 6 | 2 | YES | 1A, 2B |
| Toilets, Janitor | - | 10 | - | YES | - |
| Closets, Baths, |  |  |  |  |  |
| Showers and |  |  |  |  |  |
| Bedpan Rooms |  |  |  |  |  |
| Autopsy and | - | 15 | - | YES | - |
| Darkroom |  |  |  |  |  |
| Sterilizer Equipment | - | 10 | - | YES | - |
| Room |  |  |  |  |  |
| Laboratory (see Note | - | 6 | 2 | YES | 1A, 2B |
| 4) |  |  |  |  |  |
| Sterile Packaging | + | 4 | 2 | NO | 1A, 2B |
| Clean Storage | + | 2 | 1.1 | NO | 1A, 2B |
| Anesthesia Storage | 0 | 8 | 0 | YES | 1C |
| Decontamination or | - | 6 | - | YES | - |
| Soiled Workroom |  |  |  |  |  |
| Storage, Medical | 0 | 2 | - | NO | 1C |
| Kitchen | 0 | 20 | 7 | NO | 1C |
| Dish Storage | + | 2 | 1 | NO | 1C |
| Dish Washing | - | 10 | - | YES | - |
| Food Service Center | 0 | 6 | 1.3 | NO | 1C |
| and Dining |  |  |  |  |  |
| Dietary Storage | 0 | 2 | 1 | NO | 1C |
| Laundry | 0 | 10 | 3.3 | YES | 1C |
| Clean Linen Storage | 0 | 6 | 2 | NO | 1C |
| and Handling |  |  |  |  |  |
| Soiled Linen Storage | - | 10 | - | YES | - |
| and Handling |  |  |  |  |  |
| Storage, General | 0 | 2 | - | NO | 1C |
| Corridors | 0 | 2 | 1 | NO | 1C |
| (Non-patient) |  |  |  |  |  |
| Body Handling (see | - | 10 | - | YES | - |
| Note 2) |  |  |  |  |  |

* AIR HANDLING SYSTEM TYPES

1. Central system recirculating and redistributing air to other rooms or spaces.

2. Central system distributing 100 percent outside air.

3. Individual units with no recirculation to other rooms or spaces.

** AIR HANDLING FILTRATION LEVELS

A. 90 percent by the ASHRAE atmospheric dust spot test method.

B. 80 percent by the ASHRAE atmospheric dust spot test method.

C. 25 percent by the ASHRAE atmospheric dust spot test method.

D. Low efficiency, throw away.

E. 99.97 percent DOP

Note 1: Administrative and other staff-only areas shall be provided with outside air at the minimum rate of 20 cubic feet per minute per person, and the central system shall have a minimum of 25 percent ASHRAE dust spot efficiency filter.

Note 2: Holding rooms without body boxes must meet these requirements and be designed for a room temperature not to exceed 70 degrees Fahrenheit.

Note 3: Certain functional areas may require special ventilation consideration.

Note 4: May be recirculated to the lab but not to other parts of the hospital except for Bacteriology and Histology which must be 100 percent exhausted.

(b) Variable volume systems are permitted in all hospitals except in sensitive areas which are defined as surgical departments, obstetrical departments, laboratories, isolation rooms and critical care units and rooms.

(c) Where variable volume systems are utilized, space relative pressure requirements shall be maintained throughout the entire system control range.

(d) All air supplied to sensitive areas shall be delivered at or near the ceiling of the area served. All air removed from operating rooms, delivery rooms and nurseries shall be removed laterally near the floor level. Laminar flow systems are not to be prohibited by this requirement. At least two return or exhaust outlets shall be used in all operating rooms and delivery rooms. The bottom of the exhaust or return outlet shall be located not less than 3 inches nor more than 12 inches above the finished floor.

(e) All space having large volume exhaust hoods shall have sufficient make-up supply such that the required pressure relationship will not be adversely affected by the operation of the hood.

(f) Outdoor air intakes shall be located a minimum of 36 inches above surrounding surfaces and a minimum of 10 feet horizontally from any exhaust air and plumbing vent. Air intakes for through-the-wall air conditioners serving no more than one room are an exception to the 36-inch requirement.

(g) Unless protected by an impervious surface, acoustical and thermal internal linings composed of fibrous materials with spray-on, foil, mylar or other such surface coating materials shall not be used in ducts, air terminal devices, air handling units or other equipment serving operating rooms, delivery rooms, birthing rooms, recovery rooms, nurseries, isolation rooms and intensive care units.

(h) Smoke dampers shall be capable of being reset automatically.

(i) Condensate shall be piped to a roof drain or floor drain or shall spill onto the ground. Filters containing multimedia components shall be provided with a differential pressure gauge for each media.

(j) All filters in systems in excess of 1000 cubic feet per minute capacity shall be installed with differential pressure gauges. Multi-bank filters shall have the capability to measure differential pressure for each filter bank. Each filter gauge shall have the range of acceptable operation clearly indicated.

(k) Filters of 90 and 80 percent efficiency ratings shall be located on the discharge side of fan systems.

(l) Filter housings for 90 and 80 percent efficiency filters shall be fully gasketed and sealed with mechanical latching devices capable of exerting and maintaining a continuous, uniform sealing pressure on the filter media when in the latched, closed position.

(m) For spaces requiring positive or negative relative pressures, there shall be a minimum of 75 cubic feet per minute between the supply, return or exhaust air quantities.

(40) Psychiatric and rehabilitation hospitals shall comply with the requirements for general hospitals except as follows:

(a) Total air quantities shall be a minimum of 75 cubic feet per minute for each room.

(b) Outdoor air shall be supplied in sufficient quantities to balance air exhausted but not less than 25 cubic feet per minute per occupant.

(c) Air handler system types and filtration levels may be 1C, 2C or 3C as noted in paragraph 59A-3.081(39)(a), F.A.C.

(41) Exhaust. All fans serving exhaust systems shall be located at the discharge end of the system in all new and remodeled facilities. Fans located immediately within the building at the end of exhaust ducts shall be permitted. Existing, nonconforming systems need not be brought into compliance except in remodeling but should strive for compliance when equipment is replaced.

(a) All halon extinguishing systems shall be provided with a manually operated purge system. The purge system shall exhaust where there is no possible re-entry into the building.

(b) Each space used for administering inhalation anesthesia shall be provided with a scavenging system to vent waste gases. The system may be connected to the room exhaust system but must be exhausted to the outside.

(c) Exhaust for autopsy tables and rooms and body boxes shall be on a dedicated duct system(s) and shall discharge where re-entry into the building will be prevented.

(42) Hoods. Laboratory and Nuclear Medicine Hoods. Exhaust ducts shall be installed without fire or smoke dampers. All exhaust air ducts shall be terminated above the roof with the fan mounted on the roof. Exhaust hoods in central food preparation centers shall be listed or certified by a nationally recognized independent testing laboratory.

(43) Ducts. Except as noted in subparagraph (a) below, all new hospital outpatient surgery and cardiac catheterization facility construction shall have completely ducted air supply, return, outside air and exhaust systems including areas of other occupancies.

(a) Outpatient diagnostic and treatment facilities in buildings detached from the hospital may have plenum returns. The use of plenums does not relax the requirement of space relative pressure maintenance or smoke/fire compartment/zone neutrality.

(b) In new construction, duct system risers penetrating more than one floor shall be installed in vertical fire-rated shafts. Horizontal offsets of the risers shall not be allowed. Fire/smoke dampers shall be installed at duct penetrations of the chase.

(c) Fan and Damper Control During Fire Alarm.

1. During a fire alarm, fan systems and fan equipment shall be stopped or controlled to prevent the movement of smoke by mechanical means from the zone in alarm.

2. Fan control shall be designed so as to minimize the interruption of heating, ventilating and air conditioning in compartments remote from the compartment in alarm.

3. Fan control shall not interfere with the continuous operation of exhaust systems conveying ethylene oxide or other hazardous chemicals and fumes or systems required to operate continuously for the health and safety of occupants. Such systems shall include fume hood exhaust deemed by the governing body of the hospital to present a hazard to occupants if exhaust airflow is stopped. Air handling systems shall be designed to allow for continuous operation of all such systems and to minimize movement of smoke by mechanical means from the zone in alarm.

(44) Plumbing. All fixtures used by medical and nursing staff and all lavatories for use by patients and food handlers shall be trimmed with valves which can be operated without the use of hands and shall have a water supply spout mounted so that its discharge point is a minimum of 5 inches above the rim of the fixture. Where blade handles are used, they shall not be less than 31/2 inches or more than 4 1/2 inches in length, except that handles on clinical sinks shall not be less than 6 inches long. Scrub sinks shall have foot, knee or timer operated control valves.

(a) Clinical sinks shall be installed in all soiled utility rooms and shall have an integral trap in which the upper portion of a visible trap seal provides a water surface. Each clinical sink shall be equipped with a flush valve, a water faucet with both hot and cold water, and a bedpan rinsing device.

(b) Bedpan rinsing devices shall be provided in each patient toilet room.

(c) The above valves, spouts and bedpan rinsing devices are not required in psychiatric patient rooms except for geriatric or medical patient sleeping and treatment areas.

(d) Floor drains shall not be permitted in operating, cystoscopy and delivery rooms. Enamel finish flushing rim floor sinks may be installed in rooms used for cystoscopy procedures only.

(e) Hot water for patient use shall be maintained at a maximum temperature of 120 degrees Fahrenheit at the storage points.

(f) The location and arrangement of hand washing facilities shall permit their proper use and operation and shall not interfere with movement of the bed. Proper care should be given to the clearances required for blade type operating handles when and if they are used.

(g) Wall-mounted lavatories and hand washing facilities shall be attached to floor-mounted carriers and shall withstand an applied vertical load of a minimum of 250 pounds on the front of the fixture.

(h) There shall be a lavatory in each exam treatment room.

(i) Grease interceptors shall be located outside of the building.

(j) In nurseries where the admission/observation function is performed in the Level I nursery, there must be a medical gas alarm panel as required for critical care areas.

(k) A minimum of 4 inches of space shall be provided between the sides of wall-mounted fixtures and surfaces to either side of the fixture.

(45) Fire Pump. Where required in new construction, fire pumps and ancillary equipment shall be separated from other functions by construction having a 2-hour fire resistance rating.

(a) The fire pump normal service disconnect shall be rated to hold locked rotor current indefinitely and shall be located in compliance with National Electric Code 230-70(a) and NFPA-20, Centrifugal Fire Pumps as prescribed by Rule Chapter 4A-3, F.A.C. If the approved normal service disconnect is located on the exterior, the disconnect shall be padlocked in the “on” position. The position of the disconnect shall be supervised by connection to the fire pump remote annunciator and shall provide a separate fire alarm system trouble indication.

(b) When the fire pump is placed on the emergency system in addition to the normal supply, the emergency feeder protective device shall be sized in accordance with maximum rating or settings of NFPA-70 as prescribed by Rule Chapter 4A-3, F.A.C.

(c) The fire pump transfer switch may be either manual or automatic. If located on the line side of the controller as a separate unit, the switch must be rated for the pump motor locked rotor current indefinitely and must be located in the pump room.

(d) Combination fire pump controller and transfer switch units listed by the Underwriter’s Laboratories, Inc., as prescribed by Rule Chapter 4A-3, F.A.C., are acceptable when the transfer switch has exposable and replaceable contacts, not circuit breaker types, rated for the available short-circuit current.

(e) The fire pump shall be installed in a readily accessible location with direct access from the exterior.

(46) Electrical Requirements. General. All material, including equipment, conductors, controls, and signaling devices, shall be installed to provide a complete electrical system with the necessary characteristics and capacity to supply the electrical facility requirements as shown in the specifications and as indicated on the plans. All materials and equipment shall be listed as complying with applicable standards of Underwriter’s Laboratories, Inc., or other established standards.

(a) Nonmetallic sheathed cable or similar systems are not permitted for power and lighting wiring in any facility.

(b) Panel boards located in spaces subject to storage shall have the clear working space per NFPA-70, National Electric Code. “Electrical Access–Not For Storage” shall be permanently marked on the floor and wall about the panel. Panel boards shall not be located in egress corridors.

1. Nonmetallic raceways shall not be used or reused to serve patient care areas. Renovated patient care area branch circuitry shall be provided with an equipment ground conductor in compliance with the National Electric Code.

2. Critical care area wet locations, including cystology rooms, shall be powered through approved isolated power systems. Wet locations are defined as a patient care area that is normally subject to wet conditions while patients are present. This includes standing fluids on the floor or drenching of the work area, either of which condition is intimate to the patient or staff. Routine housekeeping procedures and incidental spillage of liquids do not define a wet location.

(c) There shall be documentation for equipotential grounding in all patient care areas, building service ground electrode systems, lightning protection ground terminals and special systems such as fire alarm, nurse call, paging, generator, emergency power and breaker coordination.

(47) Lighting. All spaces occupied by people, machinery and equipment within buildings, approaches to buildings and parking lots shall have electric lighting. Emergency lighting shall be supplied as described in NFPA-99 pursuant to Rule Chapter 4A-4, F.A.C. Selected egress emergency lighting shall be provided for the parking area and approaches to the parking area to allow safe exiting from the building area.

(a) Patient bedrooms shall have general lighting and night lighting. A reading light shall be provided for each patient. At least one luminaire for night lighting shall have a switch at the entrance to each patient room. Patient reading lights and other fixed lights not switched at the door shall have switch controls convenient for use at the luminaire. All switches for control of lighting in patient areas shall be of the quiet operating type.

(b) Operating rooms and delivery rooms shall have general lighting for the room in addition to local high intensity, specialized lighting provided by special fixtures at the surgical and obstetrical tables. Each special lighting unit for local lighting at the tables shall be connected to an independent circuit and shall be powered from the critical branch. A minimum of one general purpose lighting fixture shall be powered from a normal circuit in an operating room, delivery or similar room. A minimum of one general purpose lighting fixture in an operating room, delivery room or similar room shall be powered from the critical branch circuit.

(48) Receptacles. Every operating room and delivery room shall have a minimum of six duplex receptacles connected to the critical branch. All emergency operating rooms and outpatient operating rooms shall have a minimum of four duplex receptacles connected to the critical branch. Where mobile equipment is used which requires special electrical considerations, additional receptacles distinctively marked for specific equipment use shall be provided and connected to the critical power.

(a) Each general care patient bedroom shall have two duplex receptacles, one on each side of the head of each bed. Each receptacle shall be on a different circuit, at least one of which shall originate in a normal system panel board. There shall be one additional receptacle for motorized beds, if used, and one general purpose receptacle on another wall. There shall be a receptacle high on the footboard wall for entertainment television power. This receptacle is optional in psychiatric facilities.

(b) A maximum of six duplex receptacles shall be connected to a branch circuit over-current device.

(c) Mount general purpose receptacles at 18 inches and mount switches 48 inches above the finished floor. All dimensions are to the center line of boxes.

(d) Duplex receptacles in critical care areas, in all emergency treatment rooms and other areas – acute care beds, angiographic laboratories, cardiac catheterization laboratories, coronary care units, hemodialysis rooms or areas, emergency room treatment areas, human physiology laboratories, intensive care units and postoperative recovery rooms – shall be provided as follows:

1. There shall be a minimum of six duplex electrical receptacles for each patient station.

a. Four shall be connected to the critical branch of the essential electrical system and two of the required number shall be connected to dedicated circuits.

b. Two shall be connected to a normal power circuit except in anesthetizing locations where two shall be connected to critical power circuits.

c. There shall be no more than two receptacles per circuit.

2. All branch circuits from the emergency system shall be from the same panel board.

3. All branch circuits from the normal system shall be from the same panel board.

4. All receptacles shall have engraved cover plates to indicate the panel board and circuit numbers powering the device.

5. Branch circuit over-current devices shall be readily accessible to nursing staff and other authorized personnel.

6. Receptacles and cover plates shall be identified by a distinctive color. The color selected shall be maintained throughout the facility.

(e) Equipment in critical care areas – acute care beds, angiographic laboratories, cardiac catheterization laboratories, coronary care units, hemodialysis rooms or areas, emergency room treatment areas, human physiology laboratories, intensive care units and postoperative recovery rooms – shall be provided as follows.

1. All branch circuits powering equipment from the emergency system shall be from the same panel board.

2. All branch circuits powering equipment from the normal system shall be from the same panel board.

3. Fixed equipment shall have engraved nameplates to indicate the panel board and circuit numbers powering the equipment. Nameplates shall be permanently attached to such equipment and shall be located so as to be easily read.

4. There shall be critical power receptacles for blood bank refrigerators and a minimum of one receptacle for each pathology laboratory work counter.

(49) Fire Alarm Systems. A fire alarm annunciator panel shall be provided at a 24-hour monitored location. The panel shall indicate the zone of actuation of the alarm and there shall be a trouble signal indicator. Each smoke compartment shall be a separate fire alarm zone. A fire alarm system zone shall not include rooms or spaces in other smoke compartments and shall be limited to a maximum area of 22,500 square feet.

(50) Nurse Call System. A nurse call system shall be provided that will register a call from each patient bed to the nurse station and activate a visual signal at the patient room door and activate a visual and audible signal in the clean workroom, the soiled workroom, the nourishment station and the master station of the nursing unit. In multi-corridor nursing units, additional visible signals shall be installed at corridor intersections in the vicinity of nurse stations. In rooms containing two or more calling stations, indicating lights shall be provided for each calling station.

(a) Master staff and duty stations may include volume controls provided the minimum setting provides audibility of 15 decibels above normal ambient noise levels where the station is located.

(b) An emergency calling station of the pull cord type shall be provided and shall be conveniently located for patient use at each patient toilet, bath or shower room, but not inside the shower. The call signal shall be canceled only at the emergency calling station. The emergency station shall activate audible and visual signals immediately.

(c) An emergency resuscitation alarm calling station shall be provided for staff use in each operating, delivery, recovery LDR, LDRP, emergency, cardiac and intensive nursing care rooms, nurseries and similar rooms. Supervised wards for mental patients and pediatric bedrooms require special emergency aid calling stations.

(d) Emergency resuscitative alarm panels (centralized Code Blue) shall be provided at the attending nurse station and at other locations which are staffed 24 hours per day. Audible signals may be silenced temporarily for a call provided subsequent calls automatically reactivate the audible signal immediately. The alarm panel at the 24-hour staffed station may indicate the nurse station/suite where the call originated in lieu of identifying the bed only when a 24-hour station is not one and the same as the attending nurse station.

(51) Emergency Electric Service. An essential electrical system shall be provided in accordance with NFPA-99 (1990), Standards for Health Care Facilities, as prescribed by Rule Chapter 4A-3, F.A.C.

(a) Separate the normal main service equipment from the emergency distribution equipment by a minimum distance of 6 feet, or locate in separate rooms. Transfer switches shall be considered emergency equipment.

(b) Switches for critical branch lighting shall be totally separate from normal switching. The devices or cover plates shall be of a distinctive color. Critical branch switches may be adjacent to normal switches. Switches for life safety lighting are not permitted except as required for dusk-to-dawn automatic control of exterior lighting fixtures.

(c) There shall be selected life safety lighting arranged for automatic dusk-to-dawn operation in the parking lots and along the travel paths from the exits to safe areas. A minimum of 5 footcandles is required.

(d) A minimum of one elevator per bank serving any patient use floor shall be connected to the equipment branch of the essential electric system and arranged for manual or automatic operation during loss of normal power.

(e) There shall be a dedicated low fuel alarm for the day tank supplying the emergency generator driver. A manual pump shall also be provided for the day tank. The alarm shall be located at the generator derangement panel.

(f) Transfer switch contacts shall be of the open type and shall be accessible for inspection and replacement.

(g) There shall be power connected to the equipment branch of the essential electrical system for kitchen refrigerators, freezers and range hood exhaust fans to facilitate emergency food preparation. Selected lighting within the kitchen and dry storage areas shall be connected to the critical branch of the essential electrical system.

(h) Outpatient surgery units which are located in a separate building or on another campus shall have a Type I essential electrical system in compliance with NFPA-99, Chapters 3 and 13, Ambulatory Surgical Centers.

(52) Lightning Protection. A lightning protection system shall be provided for all new buildings and additions in accordance with NFPA-78, Lightning Protection Code, as prescribed by Rule Chapter 4A-3, F.A.C.

(a) Where additions are constructed to existing buildings, the existing building lightning protection system, if any, shall be inspected and brought into compliance with current standards.

(b) When outpatient buildings, either on or off the campus, are constructed or purchased and ambulatory surgical procedures are contemplated, a lightning protection system shall be installed.

(c) There shall be surge protection for all electrical services.

1. Main Building Power.

a. Service entrance surge arresters shall comply with National Electric Code Article 280, as prescribed by Rule Chapter 4A-3, F.A.C., and shall have integral visual indication for surge suppression failure. Additional surge protection shall be provided for all low voltage and power connections to all electronic equipment in critical care areas and life safety systems and equipment such as fire alarm, nurse call and other critical systems as listed in paragraph 59A-3.081(48)(e), F.A.C. Protection shall be in accordance with appropriate IEEE Standards for the type of equipment protected.

b. All low voltage system main or branch circuits entering or exiting the structure shall have surge suppressors installed for each pair of conductors and shall have visual indication for protector failure to the maximum extent feasible.

2. Free-standing, one-story outpatient facilities deemed not to be extraordinarily subject to lightning strikes, as determined by surrounding terrain and structures, will not be required to be provided with a lightning protection system.

(53) Physical Plant Requirements for Inpatient Cardiac Catheterization Service. The following are additional requirements for Inpatient Cardiac Catheterization Service.

(a) The number of procedure rooms and the size of the preparation, holding areas shall be based on the anticipated utilization.

1. The procedure room shall be a minimum of 400 square feet (37.16 meters) exclusive of fixed and movable cabinetry.

2. A patient preparation, holding and recovery room shall be provided and arranged to provide visual observation before and after the procedure.

3. There shall be a control room or an area shall be provided and shall be large enough to contain and provide for the efficient functioning of the X-ray and image recording equipment.

4. There shall be a view window permitting full view of the patient from the control console.

5. There shall be an equipment room or enclosure large enough to contain X-ray transformers, power modules, and associated electronics and electrical gear.

6. There shall be scrub facilities with hands-free operable controls adjacent to the entrance of procedure rooms, and shall be arranged to minimize incidental splatter on nearby personnel, medical equipment, or supplies.

7. There shall be a staff change area(s) arranged to ensure a traffic pattern so that personnel entering from outside the service area can enter, change their clothing and move directly into the cardiac catheterization suite.

8. There shall be a clean workroom or clean supply room. If the room is used for preparing patient care items, it shall contain a work counter and handwashing sink. If the room is used only for storage and holding of clean and sterile supply materials, the work counter and hand washing facilities may be omitted.

9. There shall be a soiled workroom containing a handwashing and clinical sink or equivalent flushing rim fixtures. When the room is used for temporary holding or soiled materials, the clinical sink may be omitted.

10. There shall be a housekeeping closet containing a floor receptor or service sink with provisions for storage of supplies and housekeeping equipment.

(b) The following spaces shall be available for use by the Inpatient Cardiac Catheterization Service:

1. An X-ray viewing room and;

2. An X-ray film file room.

(c) The minimum quantities and filtrations shall be met as set forth in the following table:

| INPATIENT CARDIAC CATHETERIZATION SERVICE MINIMUM VENTILATION RATE TABLE |
| --- |
|  |  |  | Outdoor | 100% | System* |
| Room or | Relative | Total | Air | Exhaust | & |
| Function | Pressure | Air | Quantities | Quantities | Filtration** |
| Preparation Room | 0 | 6 | 2 | NO | 1A, 2B |
| Recovery Room |  |  |  |  |  |
| Holding Room |  |  |  |  |  |
| Cardiac | + | 15 | 3 | NO | 1A, 2B |
| Catheterization |  |  |  |  |  |
| Procedure Room |  |  |  |  |  |
| Control Room | 0 | 4 | 2 | NO | 1A, 2B |
| Equipment Room | 0 | 4 | 0 | NO | 1A, 2B |
| Staff Changing | - | 4 | 2 | YES | 1A, 1B |
| Room |  |  |  |  |  |
| Clean Work Room | + | 4 | 2 | NO | 1A, 2B |
| Clean Supply Room | + | 4 | 2 | NO | 1A, 2B |
| Soiled Work Room | - | 10 | 2 | YES | 1A, 2B |
| Soiled Holding | - | 10 | 2 | YES | 1A, 2B |
| Room |  |  |  |  |  |

* AIR HANDLING SYSTEM TYPES

1. Central system recirculating and redistributing air to other rooms or spaces.

2. Central system distributing 100 percent outside air.

3. Individual units with no recirculation to other rooms or spaces.

** AIR HANDLING FILTRATION LEVELS

A. 90 percent by the ASHRAE atmospheric dust spot test method.

B. 80 percent by the ASHRAE atmospheric dust spot test method.

C. 25 percent by the ASHRAE atmospheric dust spot test method.

D. Low efficiency, throw away.

E. 99.97 percent DOP.

(d) The minimum medical gas station outlets shall be as follows:

| INPATIENT CARDIAC CATHETERIZATION SERVICE MEDICAL GAS STATION OUTLETS |
| --- |
| Room or |  |  |  |
| Function | Oxygen | Vacuum | Medical Air |
| Cardiac Catheterization | 1 | 2 | 2 |
| Procedure Room |  |  |  |
| Holding Room*** | 1 | 2 | 2 |
| Preparation Room*** | 1 | 2 | 2 |
| Recovery Room*** | 1 | 2 | 2 |
| *** One (01) outlet per bed or station |  |  |  |

(54) Physical Plant Requirements for Mobile Surgical Facility. The following are additional special requirements for Mobile Surgical Facilities established after July 1, 1998.

(a) Mobile Surgical Facility. A mobile surgical facility is a mobile facility as defined in Chapter 395.003, F.S., and which provides elective surgical care under contract with the Department of Corrections or a private correctional facility operating pursuant to Chapter 957, F.S.

(b) General Requirements: In addition to the codes and standards referenced in this rule, the mobile surgical facility shall comply with the requirements of Ambulatory Health Care Centers, Chapter 12-6, F.A.C., of the National Fire Protection Association (NFPA), 101 Life Safety Code, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904.

1. Site Requirements:

a. There shall be a level concrete pad designed for the structural loads of the facility in accordance with the Standard Building Code Chapter 18 & 19, incorporated by reference and available from Southern Building Code Congress International, 910 Montclair Road, Birmingham, Alabama 35213-1206.

b. There shall be walls, fences or concrete-filled steel bollards around the immediate site to prevent collisions with the unit by other vehicles.

c. The facility shall have a tie-down anchoring system designed by a Florida registered professional engineer or architect in accordance with Section H105.3, Tiedowns, Appendix H, Manufactured Home Tiedown Standards, Southern Building Code Congress International incorporated by reference and available from Southern Building Code Congress International, 910 Montclair Road, Birmingham, Alabama 35213-1206.

d. The facility shall be sited so that it does not diminish egress from the hospital and so that the exhaust from the tractor and/or generator is kept away from all fresh air intakes of the hospital.

e. There shall be a rain-free covered passage from the hospital to the entrance of the mobile facility.

2. Architectural Design Requirements:

a. There shall be an operating room with a minimum area of 170 square feet. The minimum room dimension shall be 12 feet.

b. There shall be an operating room service area containing sterilizing facilities, medication preparation and storage areas, scrub facilities, soiled work room with work counter, clean work room with storage for clean and sterile supplies, and janitor’s closet with floor receptor or service sink.

c. There shall be a recovery room/Post-Anesthetic Care Unit (PACU) adjacent to the operating room, which shall accommodate a minimum of two recovery beds. The size of this room shall be based on 80 square feet per recovery bed.

d. There shall be a nurse station for charting, communications, and storage.

e. There shall be a recovery service area containing a nourishment station, a hand washing facility, medication preparation area with refrigerator and double locked storage, clean linen storage, soiled linen area with soiled linen receptacles, and clean work area with work counter and sink.

f. There shall be an accessible patient/staff toilet room and hand wash facility adjacent to the recovery room.

g. There shall be a clothing change area for doctors, nurses and other personnel with secured storage and access to toilet room.

3. Mechanical System Requirements:

a. The Heating, Ventilating and Air Conditioning systems shall comply with NFPA 90A, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904

b. The patient gas medical systems shall be Type I as defined by NFPA 99, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904. Medical gas, vacuum, and oxygen supply systems shall comply with Chapter 13, Ambulatory Health Care Center Requirements of NFPA 99, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904.

c. The facility shall provide, as a minimum, the quantity of station outlets per bed position indicated in the following table:

| Area | Oxygen | Vacuum |
| --- | --- | --- |
| Recovery room/(PACU) | 1 | 3 |
| Operating Room | 2 | 3 |

An additional vacuum station outlet shall be provided in the operating room dedicated for connection of an anesthesia machine.

d. The plumbing systems shall comply with the Standard Plumbing Code incorporated by reference and available from Southern Building Code Congress International, 910 Montclair Road Birmingham, Alabama 35213-1206.

e. The facility shall be equipped with fire extinguishers.

4. Electrical System Requirements:

a. The essential electrical system shall comply with a Type I system as defined in Chapter 3 of NFPA 99, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904.

b. The electrical system shall comply with Article 517 of the National Electric Code, NPFA 70, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904 and with subsections 59A-3.081(46), (47), (48), (50), (51), F.A.C.

c. There shall be an automatic fire alarm system in the facility. An alarm initiated in the mobile facility shall activate the hospital fire alarm system and an alarm in the hospital shall initiate an alarm in the mobile facility.

d. There shall be a telephone connected to the hospital communication system.

e. Electrical connections to the hospital shall not interrupt, diminish or otherwise affect adversely in any way the electrical system of the hospital.

f. There shall be a lightning protection system as defined in NFPA 780, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9904, for the rain-free covered connection and the mobile facility, unless the mobile facility is shown to be within the cone of protection of the hospital and bonded to the lightning protection systems of the hospital.

5. Details and Finishes: The mobile facility shall comply with subsection 59A-3.081(31), F.A.C., Sections (i)(j), (k), (l), (m) and (p).

(55) Physical Plant Requirements for Disaster Preparedness of New Hospital Construction.

(a) Definitions. The following definitions shall apply specifically to all new facilities as used in subsection 59A-3.081(55), F.A.C.:

1. “New facility” means a hospital, or an addition of a wing or floor to an existing hospital, which has not received a Stage II Preliminary Plan approval pursuant to Chapter 59A-3, F.A.C., prior to the effective date of this rule. Interior renovation, refurbishing, modifications or conversions inside of an existing structure licensed as a hospital, shall not have to meet the standards contained in this paragraph;

2. “Net square footage” means the clear floor space of an area excluding cabinetry and other fixed furniture or equipment;

3. “During and immediately following” means a period of 72 hours following the loss of normal support utilities to the facility;

4. “Occupied patient area(s)” means the location of patients inside of the new facility or in the addition of a wing or floor to an existing facility during and immediately following a disaster;

5. “Building code” means the building codes as described in Section 553.73, F.S.

6. “Patient support area(s)” means the area(s) required to ensure the health, safety and well-being of patients during and immediately following a disaster, such as a nursing station, clean and soiled utility areas, food preparation area, and other areas as determined by the facility.

7. “On-site” means either in, immediately adjacent to, or on the campus of the facility, or addition of a wing or floor to an existing facility.

(b) New Facility Construction Standards. The following construction standards are in addition to the physical plant requirements described in subsections 079-081 of Chapter 59A-3, F.A.C. These minimum standards are intended to increase the ability of the new facility, or new floor or new wing added to an existing facility to be structurally capable of serving as a shelter for patients, staff and the family of patients and staff (as determined by the facility) and equipped to be self-supporting during and immediately following a disaster:

1. Space Standards.

a. For planning purposes, as estimated by the facility, each new facility shall provide a minimum of 30 net square feet per in-patient served in the occupied patient area(s).

b. As determined by the facility, space for administrative and support activities shall be provided for use by facility staff to allow for care of patients in the occupied patient area(s).

c. As determined by the facility, space shall be provided for staff and family members of patients and staff.

2. Site standards.

a. All new facilities and additions to existing facilities shall be located above the 100-year flood plain or hurricane Category 3 (Saffir-Simpson scale) hurricane surge inundation elevation, whichever requires the highest elevation, or;

b. The floor elevation of all new occupied patient area(s) and all patient support area(s) and patient support utilities, including mechanical, electrical except as noted in (55)9.b.(I), and food services shall be located above the 100-year flood plain or hurricane Category 3 (Saffir-Simpson scale) hurricane surge inundation elevations, whichever requires the highest elevation, or

c. New additions or floors added to existing facilities, as determined by their site locations, shall be so designed and constructed as to be in compliance with the current standards of the National Flood Insurance Program (NFIP) of the Federal Emergency Management Agency (FEMA), Technical Bulletins 1-5, 1993; FEMA 213/May 1991; 44 CFR Parts 59-78, October 1, 1997; NFIP Rules and Regulations, October and December, 1997, incorporated by reference and available from Federal Emergency Management Agency, Federal Insurance Administration, Attn. Publications, P. O. Box 70274, Washington, D.C. 20024.

d. Where an off-site public access route is available to the new facility at or above the 100-year flood plain, a minimum of one on-site emergency access route shall be provided that is located at the same elevation as the public access route;

e. New landscaping elements shall be located so if damaged they will not block the on-site emergency access route to the facility. Outdoor signs and their foundations shall be designed to meet the wind load criteria of the applicable building code;

f. New light standards and their foundations used for lighting the on-site emergency access route shall be designed to meet the wind load criteria of the American Society of Civil Engineers (ASCE 7-95), fifty-year recurrence interval of wind velocity with appropriate exposure category dependent on site location, incorporated by reference and available from the American Society of Civil Engineers, United Engineering Center, 345 East 47th Street, New York, NY 10017-2398.

3. Structural Standards. Wind load design of the building structure and exterior envelope including exterior wall systems shall be designed in accordance with the building code.

4. Roofing Standards.

a. Roofing membrane material shall resist the uplift forces specified in the building code. Roof coverings shall be installed according to the specifications provided by the manufacturer.

b. Loose-laid ballasted roofs shall not be permitted;

c. All new roof appendages such as ducts, tanks, ventilators, receivers, dx condensing units and decorative mansard roofs and their attachment systems shall be structurally engineered to meet the wind load requirements of the applicable building code. All of these attachment systems shall be connected directly to the underlying roof structure or roof support structure.

5. Exterior Unit Standards.

a. All exterior window units, skylights, exterior louvers and exterior door units including vision panels and their anchoring systems shall be designed to resist the wind load requirements of the building code and the debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130.

b. Permanently attached protective systems such as shutters and baffling shall be designed to meet the wind load requirements and the debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130;

c. Removable protective systems designed to intricately fit with the wall/window system of the facility and stored on-site at the facility and that meet the wind load requirements of the building code, and the debris impact requirements specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130 may be utilized to protect the exterior units;

d. All anchoring and attachment to the building of both the permanently attached and removable protective systems shall be designed to meet wind load requirements of the building code, and the impact requirements specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130. These designs shall be signed, sealed and dated by a registered structural engineer;

e. The glazed openings inside or outside of the protective systems shall meet the cyclical loading requirements specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130;

f. All of the exterior impact protective systems shall be designed and installed so that they do not come in contact with the glazing under uniform, impact or cyclic pressure loading;

g. When not being utilized to protect the windows, the protective system shall not restrict the operability of the windows in the occupied patient bedrooms.

h. When not being utilized to protect the windows, the protective systems shall not reduce the clear window opening below 8% of the gross square footage of the patient room.

6. Heating, Ventilation and Air Conditioning (HVAC) Standards.

a. Air moving equipment, dx condensing units, through-wall units and other HVAC equipment located outside of or on the roof of the new facility or wing or floor addition to an existing facility and providing service to the new facility or wing or floor addition to an existing facility shall be permitted only when either of the following are met:

(I) They are located inside a penthouse designed to meet the wind load requirements of the building code, or;

(II) Their fastening systems are designed to meet the wind load requirements of the building code and they are protected from impact as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130.

b. All occupied patient areas and patient support areas shall be supplied with sufficient HVAC as determined by the facility to ensure the health, safety and well being of all patients and staff during and immediately following a disaster.

c. As determined by the facility these selected HVAC systems and their associated support equipment such as a control air compressor essential to the maintenance of the occupied patient and patient support area(s) shall receive their power from the emergency power supply system(s).

d. Ventilation air change rates in occupied patient areas shall be maintained as specified in Chapter 59A-3, F.A.C., during and immediately following a disaster.

e. Auxiliary equipment and specialties such as hydronic supply piping and pneumatic control piping shall be located, routed and protected in such a manner as determined by the facility to ensure the equipment receiving the services will not be interrupted.

7. Plumbing Standards.

a. There shall be an independent on-site supply (i.e., water well) or on-site storage capability of potable water at a minimum quantity of 3 gallons per in-patient served in the new facility or wing or floor addition to an existing facility per day during and immediately following a disaster. For planning purposes the number of patients shall be estimated by the facility.

b. There shall be an independent on-site supply or storage capability of potable water at a minimum quantity of 1 gallon per facility staff, and other personnel in the new facility or wing or floor addition to an existing facility per day during and immediately following a disaster. For planning purposes, the number of these personnel shall be estimated by the facility.

c. The facility shall determine what amount of water will be sufficient to provide for patient services, and shall maintain an on-site supply or on-site storage of the determined amount.

d. When utilized to meet the minimum requirements of this rule, selected system appurtenances such as water pressure maintenance house pumps, and emergency water supply well pumps shall take power from the emergency power supply system(s).

8. Medical Gas Systems Standards. The storage, distribution piping system and appurtenances serving the occupied patient area(s) shall be contained within a protected area(s) designed and constructed to meet the structural and debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130.

9. Emergency Electrical Generator and Essential Electrical System Standards.

a. There shall be an on-site Level I emergency electrical generator system designed to support the occupied patient area(s) and patient support area(s) with at least the following support services:

(I) Ice making equipment to produce ice for the patients served, or freezer storage equipment for the storage of ice for the patients served;

(II) Refrigerator unit(s) and food service equipment if required by the emergency food plan;

(II) Life safety and critical branch lighting and systems as required by Chapter 59A-3.081, F.A.C.;

(IV) Selected HVAC systems as determined by the facility and other systems required by this rule;

b. The emergency generator system shall be fueled by a fuel supply stored on-site sized to fuel the generator for 100 percent load for 64 hours or 72 hours for actual demand load of the occupied patient area(s) and patient support area(s) and patient support utilities during and immediately following a disaster, whichever is greater.

(I) The fuel supply shall either be located below ground or contained within a protected area that is designed and constructed to meet the structural and debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130. If an underground system is utilized, it shall be designed so as to exclude the entrance of any foreign solids or liquids;

(II) All fuel lines supporting the generator system(s) for the occupied patient area(s) and patient support area(s) shall be protected also with a method designed and constructed to meet the structural and debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130.

(III) All panel boards, transfer switches, disconnect switches, enclosed circuit breakers or emergency system raceway systems required to support the occupied patient area(s), patient support area(s) or support utilities shall be contained within a protected area(s) designed and constructed to meet the structural and debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130, and shall not rely on systems or devices outside of this protected area(s) for their reliability or continuation of service.

(IV) The emergency generator(s) shall be air or self-contained liquid cooled and it and other essential electrical equipment shall be installed in a protected area(s) designed and constructed to meet the structural and debris impact requirements as specified by Section 2315 of the South Florida Building Code, Dade edition 1994, incorporated by reference and available from the Metropolitan Dade County Building Code Compliance Department, 140 West Flagler Street, Suite 1603, Miami, FL 33130.

10. Fire Protection Standards.

a. If the facility requires fire sprinklers as part of its fire protection, either of the following shall be met:

(I) On-site water storage capacity to continue sprinkler coverage, in accordance with the requirements of NFPA 13, 1996 edition, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9101 or,

(II) If the facility plans to provide a fire watch, it shall use the following procedure as approved by the Office of Plans and Construction for all areas of the facility that are without sprinkler coverage due to interrupted water flow.

(A) Notify the local fire department and document instructions.

(B) Notify the Agency through the Area Office.

(C) Assess the extent of the condition and effect corrective action, with a documented time frame. If the corrective action will take more than four (4) hours, do the following items:

I. Implement a contingency plan to the facility fire plan containing: a description of the problem, specifically what the system is not doing that it normally does, and the projected correction time frame. All staff on shifts involved shall have documented in-servicing and drilling for the contingency.

II. Begin a documented fire watch, until the system is restored. Persons used for fire watch must be trained in what to look for, what to do, and be able to expeditiously contact the fire department. For a fire watch, a facility can use only: public safety persons (i.e., fire service), a guard service, or staff (e.g., a nurse, maintenance, drill or safety coordinator); if the persons are:

A. Off duty from their regular position; in compliance with current state staffing ratios and personnel policies (i.e., not in a condition that would impair performance);

B. Trained and competent in what to look for and what to do;

C. Have a provision for priority communication (i.e., a radio or special telephone).

D. Notify Agency and local authorities, if the time-frame changes or system is restored.

b. If the facility provides a fire watch in lieu of sprinkler on-site water or water storage, then one 4-A type fire extinguisher or equivalent shall be provided for every 3 or less 2-A fire extinguishers required by NFPA 10, 1998 edition, incorporated by reference and available from NFPA, 1 Batterymarch Park, P. O. Box 9101, Quincy, MA 02269-9101, for the area served. These additional extinguishers shall be equally distributed throughout the area they are protecting.

11. External Emergency Communications Standards. Each new facility shall provide for external electronic communication not dependent on terrestrial telephone lines, cellular, radio or microwave towers, such as on-site radio transmitter, satellite communication systems or a written agreement with an amateur radio operator volunteer group(s). This agreement shall provide for a volunteer operator and communication equipment to be re-located into the facility in the event of a disaster until communications are restored. Other methods which can be shown to maintain uninterrupted electronic communications not dependent on land-based transmission shall be pre-approved by the Office of Plans and Construction.

Rulemaking Authority 395.0163, 395.1055, 408.036, 400.23 FS. Law Implemented 395.0163, 395.1031, 395.1055, 400.23, 408.036 FS. History–New 1-1-77, Formerly 10D-28.81, Amended 1-16-87, 11-23-88, Formerly 10D-28.081, Amended 9-3-92, 6-29-97, 3-18-98, 11-29-99, 12-20-99, 5-25-00.

## 59A-3.110 Services.

Services shall be designed to meet the needs of the emotionally disturbed patient and must conform to stated purposes and objectives of the program.

(1) Intake and Admission.

(a) Acceptance of a child or adolescent for inpatient treatment shall be based on the assessment, arrived at by the multidisciplinary clinical staff involved and clearly explained to the patient and the family. Whether the family voluntarily requests services or the patient is referred by the court, the special hospital shall involve the family’s participation to the fullest extent possible. Discharge planning shall begin at the time of intake and admission.

(b) Acceptance of the child or adolescent for treatment shall be based on the determination that the child or adolescent requires treatment of a comprehensive and intensive nature and is likely to benefit by the programs that the facility has to offer.

(c) Admission shall be in keeping with stated policies of the special hospital and shall be limited to those patients for whom the special hospital is qualified by staff, program and equipment to give adequate care.

(d) Staff members who will be working with the patient, but who did not participate in the initial assessment shall be oriented regarding the patient and the patient's anticipated admission prior to meeting the patient. When the patient is to be assigned to a group, the other patients in the group shall be prepared for the arrival of the new member. There shall be a specific staff member assigned to the new patient to observe him and help with the unit orientation period.

(e) The admission procedure shall include documentation concerning:

1. Responsibility for and amount of financial support;

2. Responsibility for medical and dental care, including consent for medical and surgical care and treatment;

3. Arrangements for appropriate family participation in the program, phone calls and visits when indicated;

4. Arrangements for clothing, allowances and gifts; and

5. Arrangements regarding the patient’s leaving the facility with or without medical consent.

(f) Decisions for admission shall be based on the initial assessment of the patient made by the appropriate multidisciplinary clinical staff. This assessment must be documented on the record of treatment on admission.

(g) The admission order must be written by a staff or consultant physician.

(2) Assessment and Treatment Planning Including Discharge.

(a) Assessment. The facility is responsible for a complete assessment of the patient, some of which may be required just prior to admission, by professionals acceptable to the facility’s staff. The complete assessment shall include:

1. Physical. Subparagraphs a., b. and c. must be completed by a physician on the staff of the facility prior to admission or within 24 hours after admission.

a. Complete medical history, including history of medications;

b. General physical examinations;

c. Neurological assessment;

d. Motor development and functioning;

e. Dental assessment;

f. Speech, hearing and language assessment;

g. Vision assessment;

h. Review of immunization status and completion according to the U.S. Public Health Service Advisory Committee on Immunization Practices and the Committee on Control of Infectious diseases of the American Academy of Pediatrics;

i. Laboratory workup including routine blood work and analysis;

j. Chest x-ray and/or tuberculin test;

k. Serology; and

l. Urinalysis.

m. If any of the physical health assessments indicate the need for further testing or definitive treatment, arrangements shall be made to carry out or obtain the necessary evaluations or treatment by clinicians or physicians trained as applicable, and plans for these treatments shall be coordinated with the patient’s overall treatment plan.

2. Psychiatric/Psychological.

a. The assessment includes direct psychiatric evaluation and behavioral appraisal, evaluation of sensory, motor functioning, a mental status examination appropriate to the age of the patient and a psychodynamic appraisal. A psychiatric history, including history of any previous treatment for mental, emotional or behavioral disturbances shall be obtained, including the nature, duration and results of the treatment, and the reason for termination.

b. The psychological assessment includes appropriate testing.

3. Developmental/Social.

a. The developmental history of the patient includes the prenatal period and from birth until present, the rate of progress, developmental milestones, developmental problems, and past experiences that may have affected the development. The assessment shall include an evaluation of the patient’s strengths as well as problems. Consideration shall be given to the healthy developmental aspects of the patient, as well as to the pathological aspects, and the effects that each has on the other shall be assessed. There shall be an assessment of the patient’s current age, appropriate developmental needs, which shall include a detailed appraisal of his peer and group relationships and activities.

b. The social assessment includes evaluation of the patient’s relationships within the structure of the family and with the community at large, and evaluation of the characteristics of the social, peer group, and institutional settings from which the patient comes. Consideration shall be given to the patient’s family circumstances, including the constellation of the family group, their current living situation, and all social, religious, ethnic, cultural, financial, emotional and health factors. Other factors that shall be considered are past events and current problems that have affected the patient and family; potential of the family’s members meeting the patient’s needs; and their accessibility to help in the treatment and rehabilitation of the patient. The expectations of the family regarding the patient’s treatment, the degree to which they expect to be involved, and their expectations as to the length of time and type of treatment required shall be assessed.

4. Nursing. The nursing assessment shall be performed by a person, who at a minimum, is duly licensed in the State of Florida to practice as a registered nurse and shall include the evaluation of:

a. Self-care capabilities including bathing, sleeping, eating;

b. Hygienic practices such as routine dental and physical care and establishment of healthy toilet habits;

c. Dietary habits including a balanced diet and appropriate fluid and calorie intake;

d. Response to physical diseases (e.g., acceptance by the patient of a chronic illness as manifested by his compliance with prescribed treatment);

e. Responses to physical handicaps (e.g., the use of prostheses for coping patterns used by the visually handicapped); and

f. Responses to medications (e.g., allergies or dependence).

5. Educational/Vocational. The patient’s current educational/vocational needs in functioning, including deficits and strengths, shall be assessed. Potential educational impairment and current and future educational vocational potential shall be evaluated using, as indicated, specific educational testing and special educators or others.

6. Recreational. The patient’s work and play experiences, activities, interests and skills shall be evaluated in relation to planning appropriate recreational activities.

(b) Treatment Planning. An initial treatment plan shall be formulated, written and interpreted to the staff and patient within 72 hours of admission. The comprehensive treatment plan shall be developed for each child by a multidisciplinary staff, within 14 days of admission. This plan must be reviewed at least monthly, or more frequently if the objectives of the program indicate. Review shall be noted in the record. A psychiatrist as well as multidisciplinary professional staff must participate in the preparation of the plan and any major revisions.

1. The treatment plan shall be based on the assessment and shall include clinical consideration of the physical, developmental, psychological, chronological age, family, education, social and recreational needs. The reason for admission shall be specified as shall specific treatment goals, stated in measurable terms, including a projected time frame, treatment modalities to be used, staff who are responsible for coordinating and carrying out the treatment, and expected length of stay and designation of the person or agency to whom the child will be discharged.

2. The degree of the family's involvement (parent or parent surrogates) shall be defined in the treatment planning program.

3. Collaboration with resources and significant others shall be included in treatment planning, when the treatment team determines it will not interfere with the child’s treatment.

4. Procedures that place the patient at physical risk or pain shall require special justification. The rationale for their use shall be clearly set forth in the treatment plan and shall reflect the prior involvement and specific review of the treatment plan by a child psychiatrist. When potentially hazardous procedures or modalities are contemplated for treatment, there shall be additional program specific policies governing their use to protect the rights and safety of the patient. The facility shall have specific written policies and procedures governing the use of electroconvulsive therapy or other forms of convulsive therapy. If such procedures are to be used they shall be carried out in a setting with emergency equipment available and shall be administered only by medical personnel who have been trained in the use of such equipment. Policies and procedures shall insure that:

a. Electroconvulsive therapy or other forms of convulsive therapy shall not be administered to any patient unless, prior to the initiation of treatment, two child psychiatrists with training or experience in the treatment of adolescents, who are not affiliated with the treating facility, have examined the patient, consulted with the responsible child psychiatrist and have written and signed reports which show concurrence with the administration of such treatment. Such reviews shall be carried out only by American Board of Psychiatry certified or American Board of Psychiatry eligible child psychiatrists;

b. All signed consultation reports, either recommending or opposing the administration of such treatment, shall be made a part of the patient’s clinical record;

c. Written informed consent of members of the family authorized to give consent, and where appropriate the patient’s consent shall be obtained and made a part of the patient’s clinical records. The person who is giving such consent may withdraw consent at any time;

d. Lobotomies or other surgical procedures for intervention or alterations of a mental, emotional or behavioral disorder shall not be performed on patients.

(c) Discharge. Discharge planning begins at the time of admission. A discharge date shall be projected in the treatment plan. Discharges shall be signed by a staff physician of the facility. A discharge summary shall be included in the records. Discharge planning shall include input from the multidisciplinary staff and will include family participation.

1. Discharge planning shall include a period of time for transition into the community (e.g., home visits gradually lengthened) for those patients who have been in the program for six months or longer. There must be a written plan for follow-up services, either by the facility or by another agency.

(3) Staff Coverage. There shall be a master clinical staffing pattern which provides for adequate clinical staff coverage at all times.

(a) There shall be at least one registered nurse on duty at all times. Services of a registered nurse shall be available for all patients at all times.

(b) A physician shall be on call twenty-four (24) hours a day and accessible to the facility within forty-five (45) minutes.

(c) Special attention shall be given to times which probably indicate the need for increased direct care (e.g., weekends, evenings, during meals, transition contained herein, and substantiated by the results between activities, and waking hours).

(d) Staff interaction shall insure that there is adequate communication of information regarding patients (e.g., between working shifts or change of personnel) with consulting professional staff for routine planning and patient review meetings. These interactions shall be documented in writing.

(4) Program Activities. Program goals of the facility shall include those activities designed to promote the physical and emotional growth and development of the patients, regardless of pathology or age level. There should be positive relationships with general community resources, and the facility staff shall enlist the support of these resources to provide opportunities for patients to participate in normal community activities as they are able. All labeling of vehicles used for transportation of patients shall be such that it does not call unnecessary attention to the patients.

(a) Group Size. The size and composition of each living group shall be therapeutically planned and depend on the age, developmental level, sex and clinical conditions. It shall allow for staff-patient interaction, security, close observation and support.

(b) Routine Activities. Basic routine shall be delineated in a written plan which shall be available to all personnel. The daily program shall be planned to provide a consistent well structured yet flexible framework for daily living and shall be periodically reviewed and revised as the needs of the individual patient or the living group change. Basic daily routine shall be coordinated with special requirements of the patient’s treatment plan.

(c) Social and Recreation Activities. Program of recreational and social activities shall be provided for all patients for daytime, evenings and weekends, to meet the needs of the patients and goals of the program. There shall be documentation of these activities as well as schedules maintained of any planned activities.

(d) Religious Activities. Opportunity shall be provided for all patients to participate in religious services and other religious activities within the framework of their individual and family interests and clinical status. The option to celebrate holidays in the patient's traditional manner shall be provided and encouraged.

(e) Education. The facility shall arrange for or provide an educational program for all patients receiving services in that facility.

1. The particular educational needs of each patient shall be considered in both placement and programming.

2. Children or adolescents placed in the special hospital by a public agency or at the expense of a public agency shall receive education consistent with the requirements of Chapter 6A-15 or Chapter 6A-6, F.A.C., as applicable.

(f) Vocational Programs. The facility shall arrange for, or provide, vocational or prevocational training for patients in the facility for whom it is indicated.

1. If there are plans for work experience developed as part of the patient’s overall treatment plan, the work shall be in the patient’s interest with payment where appropriate, as determined by the treatment facility and the vocational program, and never solely in the interest of the facility’s goals or needs.

2. Patients shall not be solely responsible for any major phase or institutional operation or maintenance, such as cooking, laundering, housekeeping, farming or repairing. Patients shall not be considered as substitutes for employed staff.

(g) Nutrition and Standards. There shall be a provision of planning and preparation of special diets as needed (e.g., diabetic, bland, high calorie). Menus shall be evaluated by a consultant dietitian relative to nutritional adequacy at least monthly, with observation of food intake and changes seen in the patient.

(5) Physical Care. The facility shall have available, either within its own organizational structure or by written agreements or contracts with outside health care clinicians or facilities, a full range of services for the treatment of illnesses and the maintenance of general physical health.

(a) The facility shall develop a written plan for medical services which delineates the ways the facility obtains or provides all general and specialized medical, surgical, nursing, pharmaceutical and dental services.

1. Insofar as Rules 59A-3.100 through 59A-3.111, F.A.C., are intended to establish minimum requirements for intensive residential treatment programs for children and adolescents that have a primary purpose of treating emotional and mental disorders, such facilities are not required to establish and maintain medical buildings and equipment required of general or specialty hospitals as specified in Rules 59A-3.200 through 59A-3.232, F.A.C. Services which require such specialized buildings and equipment may be obtained from outside health care providers by written agreement or contract. This shall not preclude the facility from maintaining a medical services area or building which does not meet the requirements of Rules 59A-3.200 through 59A-3.232, F.A.C., for the purpose of isolating patients with contagious diseases, conducting physical examinations, providing preventive medical care services, or providing first aid services.

2. If the facility chooses to establish and operate a specialty or general hospital for the purposes of offering medical care more intensive than those specified in subsection 59A-3.201(32), F.A.C., the plans for construction shall be submitted for review in accordance with Rule 59A-3.080, F.A.C., and such facilities shall be required to be licensed, built and operated in accordance with Rules 59A-3.200-.232, F.A.C.

(b) Patients who are physically ill may be cared for on the grounds of the facility if medically feasible as determined by a physician. If medical isolation is necessary, there shall be sufficient and qualified staff available to provide care and attention.

(c) Provisions shall be made in writing for patients from the facility to receive care from outside health care providers and hospital facilities, in the event of serious illness which the facility cannot properly handle. Such determinations shall be made by a licensed physician.

(d) Every patient shall have a complete physical examination annually and more frequently if indicated. This examination shall be as inclusive as the initial examination. Efforts shall be made by the institution to have physical defects of the patients corrected through proper medical care. Immunization shall be kept current (DT, polio, measles, mumps, M-M-R).

(e) Each member of the program staff shall be trained to recognize common symptoms of the illnesses of patients, and to note any marked dysfunctions of patients.

(f) Staff shall have knowledge of basic health needs and health problems of patients, such as mental health, physical health and nutritional health. Staff shall teach attitudes and habits conducive to good health through daily routines, examples and discussion, and shall help the patients to understand the principles of health.

(g) Each program shall have a planned program of dental care and dental health which shall be consistently followed. Each patient shall receive a dental examination by a qualified dentist and prophylaxis at least once a year. Reports of all examinations and treatment shall be included in the patient’s clinical record.

(6) Emergency Services. All clinical staff shall have training in matters related to handling emergency situations.

(a) Policies and procedures shall be written regarding handling and reporting of emergencies and these shall be reviewed at least yearly thereafter by all staff.

(b) There shall be a physician on call twenty-four (24) hours a day; his name and where he can be reached shall be clearly posted in accessible places for program staff.

(c) All direct service program staff must maintain current first aid certificate.

(d) An emergency medication kit shall be made available and shall be constituted to meet the needs of the facility. The emergency medication kit shall contain items selected by the staff or consultant medical doctor and staff or consultant pharmacist which shall be maintained and safeguarded in accordance with federal and state laws and regulations pertaining to the specific drug items included.

(e) There shall be an adequate number of first aid kits available to program staff at all times. Contents of the first aid kits shall be selected by the staff or consultant medical personnel and shall include items designed to meet the needs of the facility.

(f) The program shall have written policies and procedures of obtaining emergency diagnosis and treatment of dental problems. The program shall have written agreement with a licensed dentist(s) who is a consultant or a member of the staff for emergency dental care.

(g) The facility shall have a written plan to facilitate emergency hospitalization in a licensed medical facility. The facility shall make available a written agreement from a licensed hospital verifying that routine and emergency hospitalization will be provided.

(h) The special hospital shall have a written plan for providing emergency medical and psychiatric care.

1. There shall be a written posted plan which shall clearly specify who is available and authorized to provide necessary emergency psychiatric or medical care, or to arrange for referral or transfer to another facility to include ambulance arrangements, when necessary.

2. There shall be a written plan regarding emergency notification to the parents or legal guardian. This plan and arrangements shall be discussed with all families or guardians of patients upon admission.

(7) Pharmaceutical Services. Pharmaceutical services, if provided, shall be maintained and delivered as described in the applicable sections of Chapter 465, F.S., Chapter 893, F.S., Chapter 500, F.S., and Board of Pharmacy Chapter 21S, F.S.

(8) Laboratory and Pathology Services.

(a) The facility shall provide clinical and pathology services within the institution, or by contractual arrangement with a laboratory commensurate with the facility’s needs and which is registered under the provisions of Chapter 483, F.S.

1. Provision shall be made for the availability of emergency laboratory services 24 hours a day, 7 days a week, including holidays.

2. All laboratory tests shall be ordered by a physician.

3. All laboratory reports shall be filed in the patient’s medical record.

4. The facility shall have written policies and procedures governing the collection, preservation and transportation of specimens to assure adequate stability of specimens.

(b) Where the facility depends on an outside laboratory for services, there shall be a written contract detailing the conditions, procedures and availability of work performed. The contract shall be reviewed and approved by the medical staff, administrator and the governing body.

(9) Patients’ Rights. Every effort shall be made to safeguard the legal and civil rights of patients and to make certain that they are kept informed of their rights, including the right to legal counsel and all other requirements of due process.

(a) Individual dignity and human rights are guaranteed to all clients of mental health facilities in Florida by the Florida Mental Health Act, known as the “Baker Act,” Chapter 394, F.S.

(b) Each facility shall be administered in a manner that protects the client’s rights, his life, and his physical safety while under treatment.

1. The special hospital’s space and furnishings should be designed and planned to enable the staff to respect the patient’s right to privacy and, at the same time, provide adequate supervision according to the development and clinical needs of the patients. Provisions for an individual patient’s rights regarding privacy shall be made explicit to the patient and family. A written policy concerning patient’s rights shall be provided to the patient of authentic research or studies, or innovations of client’s record.

2. The special hospital center’s policies shall allow patient visitation and communication with all members of the family and other visitors as clinically indicated and when such visits are consistent with the facility’s program. When therapeutic considerations recommended by the responsible licensed psychologist or physician necessitate restriction of communication or visits, as set forth in the programs policies and procedures, these restrictions shall be evaluated at least weekly by the clinical staff for their continuing effectiveness. These restrictions shall be documented and signed by the responsible psychologist or physician and be placed in the patient’s record. The special hospital shall make known to the patient, the family and referring agency its policies regarding visiting privileges on and off the premises, correspondence and telephone calls. These policies shall be stated in writing and shall be provided to the patient and family and updated when change in policy occurs. When limitations on such visits, calls or other communications are indicated by practical reason, e.g., the expense of travel or telephone calls, such limitations shall be determined with participation of the patient’s family or guardian.

3. Patients shall be allowed to request an attorney through their parents or guardians. This shall be established as written policy, and the policy shall be provided to families and patients.

4. Patient’s opinions and recommendations shall be considered in the development and continued evaluation of the therapeutic program. The special hospital shall have written policies to carry out appropriate procedures for receiving and responding to patient communications concerning the total program.

5. The special hospital shall have written policies regarding methods used for control of patients’ behavior. Such written policies shall be provided to the appropriate staff and to the patient and his family. Only staff members responsible for the care and treatment of patients shall be allowed to handle discipline. Patients shall not be subject to cruel, severe, unusual or unnecessary punishment. Patients shall not be subjected to remarks which ridicule them or their families, or others.

6. Protective restraint consists of any apparatus or condition which interferes with the free movement of the patient. Only in an emergency shall physical holding be employed unless there are physician’s orders for a mechanical restraint. Physical holding or mechanical restraints, such as canvas jackets or cuffs, shall be used only when necessary to protect the patient from injury to himself or others. Use of mechanical restraints reflect a psychiatric emergency and must be ordered by the responsible staff/consultant physician, be administered by trained staff and be documented in the patient’s clinical records. The need for the type of restraint used and the length of time it was employed and condition of the patient shall be recorded in the patient’s record. An order for a mechanical restraint shall designate the type of restraint to be used, the circumstance under which it is to be used and the duration of its use. A patient in a mechanical restraint shall have access to a staff member at all times during the period of restraint.

7. The facility shall have written policies and procedures which govern the use of seclusion. The use of seclusion shall require clinical justification and shall be employed only to prevent a patient from injuring himself or others, or to prevent serious disruption of the therapeutic environment. Seclusion shall not be employed as punishment or for the convenience of staff. A written order from a physician shall be required for the use of seclusion for longer than one hour. Written orders for seclusion shall be limited to twenty-four (24) hours. The written approval of the medical director or the director of psychiatrist services shall be required when seclusion is utilized for more than twenty-four (24) hours. Staff who implement written orders for seclusion shall have documented training in the proper use of the procedures. Appropriate staff shall observe and visually monitor the patient in seclusion every fifteen (15) minutes, documenting the patient’s condition and identifying the time of observation. A log shall be maintained which will record on a quarter- hour basis the observation of the patient in seclusion, and will also indicate when the patient was taken to the bathroom, when and where meals were served, when other professional staff visited, etc., and shall be signed by the observer. The need or reason for seclusion shall be made clear to the patient and shall be recorded in the patient’s clinical record. The length of time in seclusion shall also be recorded in the clinical record, as well as the condition of the patient. A continuing log shall be maintained by the facility that will indicate by name the patients placed in seclusion, date, time, specified reason for seclusion and length of time in seclusion. In an emergency, orders may be given by a physician over the telephone to a registered professional nurse. Telephone orders must be reviewed within twenty-four (24) hours by the director of psychiatric services.

8. The special hospital shall not exploit a patient or require a patient to make public statements to acknowledge his gratitude to the treatment center.

9. Patients shall not be required to perform at public gatherings.

10. The special hospital shall not use identifiable patients’ pictures without written consent. The signed consent form shall be on file at the facility before any such pictures are used. A signed consent form must indicate how pictures shall be used and a copy shall be placed in the patient’s clinical record.

(10) Records. The form and detail of the clinical records may vary but shall minimally conform to the following standards:

(a) Content. All clinical records shall contain all pertinent clinical information and each record shall include but not be limited to:

1. Identification data and consent forms; when these are not obtainable, reason shall be noted;

2. Source of referral;

3. Reason for referral, example, chief complaint, presenting problem;

4. Record of the complete assessment;

5. Initial formulation and diagnosis based upon the assessment;

6. Written treatment plan;

7. Medication history and record of all medications prescribed;

8. Record of all medication administered by facility staff, including type of medication, dosages, frequency of administration, persons who administered each dose, and route of administration;

9. Documentation of course of treatment and all evaluations and examinations, including those from other facilities, for example, emergency rooms or general hospitals;

10. Periodic treatment summaries; updated at least every 90 days;

11. All consultation reports;

12. All other appropriate information obtained from outside sources pertaining to the patient;

13. Discharge or termination summary report; and

14. Plans for follow-up and documentation of its implementation.

(b) Identification data and consent form shall include the patient’s name, address, home telephone number, date of birth, sex, next of kin, school and what grade, date of initial contact or admission to the program, legal status and legal document, and other identifying data as indicated.

(c) Progress Notes. Progress notes shall include regular notations at least weekly by staff members, consultation reports and signed entries by authorized identified staff. Progress notes by the clinical staff shall:

1. Document a chronological picture of the patient’s clinical course;

2. Document all treatment rendered to the patient;

3. Document the implementation of the treatment plan;

4. Describe each change in each of the patient’s conditions;

5. Describe responses to and outcome of treatment; and

6. Describe the responses of the patient and the family or significant others to significant inter-current events.

(d) Discharge Summary. The discharge summary shall include the initial formulation and diagnosis, clinical resume, final formulation and final primary and secondary diagnoses, the psychiatric and physical categories. The final formulation shall reflect the general observations and understanding of the patient’s condition during appraisal of the fundamental needs of the patients. The relevant discharge diagnoses shall be recorded and coded in the standard nomenclature of the current “Diagnostic and Statistical Manual of Mental Disorders,” published by the American Psychiatric Association, and the latest edition of the “International Classification of Diseases,” regardless of the use of other additional classification systems. Records of discharged patients shall be completed following discharge within a reasonable length of time, and not to exceed 15 days. In the event of death, a summation statement shall be added to the record either as a final progress note or as a separate resume. This final note shall take the form of a discharge summary and shall include circumstances leading to death. All discharge summaries must be signed by a staff or consultant physician.

(e) Recording. Entries in the clinical records shall be made by staff having pertinent information regarding the patient, consistent with the facility policies, and authors shall fully sign and date each entry. When mental health trainees are involved in patient care, documented evidence shall be in the clinical records to substantiate the active participation of supervisory clinical staff. Symbols and abbreviations shall be used only when they have been approved by the clinical staff and when there is an explanatory notation. Final diagnosis, both psychiatric and physical, shall be recorded in full, and without the use of either symbols or abbreviations.

(f) Policies and Procedures. The facility shall have written policies and procedures regarding clinical records which shall provide that:

1. Clinical records shall be confidential, current and accurate;

2. The clinical record is the property of the facility and is maintained for the benefit of the patient, the staff and the facility;

3. The facility is responsible for safeguarding the information in the record against loss, defacement, tampering or use by unauthorized persons;

4. The facility shall protect the confidentiality of clinical information and communication between staff members and patients;

5. Except as required by law, the written consent of the patient, family, or other legally responsible parties, is required for the release of clinical record information;

6. Records may be removed from the facility's jurisdiction and safekeeping only according to the policies of the facility or as required by law; and

7. That all staff shall receive training, as part of new staff orientation and with periodic update, regarding the effective maintenance of confidentiality of the clinical record. It shall be emphasized that confidentiality refers as well to discussions regarding patients inside and outside the facility. Verbal confidentiality shall be discussed as part of all employee training.

(g) Maintenance of Records. Each facility shall provide for a master filing system which shall include a comprehensive record on each patient’s involvement in every program aspect.

1. Appropriate records shall be kept on the unit where the patient is being treated or be directly and readily accessible to the clinical staff caring for the patient;

2. The facility shall maintain a system of identification and coding to facilitate the prompt location of the patient’s clinical records;

3. There shall be policies regarding the permanent storage, disposal or destruction of the clinical records of disclosure of confidential information later in life;

4. The clinical record services required by the facilities shall be directed, staffed and equipped to facilitate the accurate processing, checking, indexing, filing, retrieval and review of all clinical records. The clinical records service shall be the responsibility of an individual who has demonstrated competence and training or experience in clinical record administrative work. Other personnel shall be employed as needed, in order to effect the functions assigned to the clinical record services;

5. There shall be adequate space, equipment and supplies, compatible with the needs of the clinical record service, to enable the personnel to function effectively and to maintain clinical records so that they are readily accessible.

(11) Program and Patient Evaluation. The staff shall work towards enhancing the quality of patient care through specified, documented, implemented and ongoing the designing professions having as their purpose processes of clinical care evaluation studies and utilization review mechanisms.

(a) Individual Case Review.

1. There shall be regular staff meetings or unit meetings to review and monitor the progress of the individual child or adolescent patient. Each patient’s case shall be reviewed within a month after admission and at least monthly during residential treatment. This shall be documented. This meeting may also be used for review and revision of treatment plans.

2. The facility shall provide for a follow-up review on each discharged patient to determine effectiveness of treatment and disposition.

(b) Program Evaluation.

1. Clinical Care Evaluation Studies. There shall be evidence of ongoing studies to define standards of care consistent with the goals of the program effectiveness of the program, and to identify gaps and inefficiencies in service. Evaluation shall include follow-up studies. Studies shall consist of the following elements:

a. Selection of an appropriate design;

b. Specification of information to be included;

c. Collection of data;

d. An analysis of data with conclusions and recommendations;

e. Transmissions of findings; and

f. Follow-up on recommendations.

2. Utilization Review. Each facility shall have a plan for and carry out utilization review. The review shall cover the appropriateness of admission to services, the provision of certain patterns of services, and duration of services. There shall be documentation of utilization review meetings either in minutes or in individual clinical records. The improvement of patient care, shall receive special consideration following a request and documentation of the proposed project by the individual sponsor.

Rulemaking Authority 395.1055 FS. Law Implemented 395.001, 395.1055 FS. History–New 1-1-77, Formerly 10D-28.92, 10D-28.110, Amended 9-4-95.

## 59A-3.2085 Department and Services.

(1) Nutritional Care. All licensed hospitals shall have a dietetic department, service or other similarly titled unit which shall be organized, directed and staffed, and integrated with other units and departments of the hospitals in a manner designed to assure the provision of appropriate nutritional care and quality food service.

(a) The dietetic department shall be directed on a full-time basis by a registered dietitian or other individual with education or specialized training and experience in food service management, who shall be responsible to the chief executive officer or his designee for the operations of the dietetic department.

(b) If the director of the dietetic department is not a registered dietitian, the hospital shall employ a registered dietitian on at least a part-time or consulting basis to supervise the nutritional aspects of patient care and assure the provision of quality nutritional care to patients. The consulting dietitian shall regularly submit reports to the chief executive officer concerning the extent of services provided.

(c) Whether employed full-time, part-time or on a consulting basis, a registered dietitian shall provide at least the following services to the hospital on the premises on a regularly scheduled basis:

1. Liaison with administration, medical and nursing staffs;

2. Patient and family counseling as needed;

3. Approval of menus and modified diets;

4. Required nutritional assessments;

5. Participation in development of policies, procedures and continuing education programs; and

6. Evaluation of dietetic services.

(d) At least annually, a registered dietitian shall conduct a review and evaluation of the dietetic department to include:

1. A review of menus for nutritional adequacy;

2. A review of tray identification methods, patients who are not receiving oral intake, and the elapsed time between the evening meal and the next substantial meal;

3. A review of the counseling and instruction given to patients and their families with special dietary needs;

4. A review of committee activities concerning nutritional care; and

5. A review of the appearance, palatability, serving temperature, patient acceptability and choice, and retention of nutrient value of food served by the dietetic department.

(e) Nothing in this section shall prevent a hospital from employing an outside food management company for the provision of dietetic services, provided the requirements of this section are met, and the contract specifies this compliance.

(f) The dietetic department, service or other similarly titled unit shall employ sufficient qualified personnel under competent supervision to meet the dietary needs of patients.

(g) Personnel in the dietetic department shall receive, as appropriate to their level of responsibility, instruction in:

1. Personal hygiene and infection control;

2. Food handling, preparation, serving and storage; cleaning and safe operation of equipment;

3. Waste disposal;

4. Portion control;

5. Diet instruction; and

6. The writing of modified diets and the recording of pertinent dietetic information in the patient’s medical record.

(h) Personnel in the dietetic department shall receive at least quarterly in-service training of which a record shall be kept by the dietetic department.

(i) The dietetic department, service or other similarly titled unit shall be guided by written policies and procedures that cover food procurement, preparation and service. Dietetic department policies and procedures shall be developed by the director of the dietetic department with nutritional care policies and procedures developed by a registered dietitian, shall be subject to annual review, revised as necessary, dated to indicate the time of last review, and enforced. Written dietetic policies shall include at least the following:

1. A description of food purchasing, storage, inventory, preparation, service, and disposal policies and procedures.

2. A requirement that diet orders be recorded in the patient’s medical record by an authorized individual before the diet is served to the patient.

3. The proper use and adherence to standards for nutritional care as specified in the diet manual which is at least in accordance with the Recommended Dietary Allowances (1989) of the Food and Nutrition Board, National Research Council and National Academy of Sciences.

4. A requirement for patients who are on oral intake and do not have specific dietary requirements, that at least three meals or their equivalent be provided daily, with not more than a 15 hour span between the evening meal and breakfast.

5. A requirement that temperatures for holding and serving cold foods be below 45 degrees F, and for hot foods be above 140 degrees F.

6. A requirement that a supply of non-perishable foods sufficient to serve a hospital’s patients for at least a one week period be available.

7. A requirement that written reports of sanitary inspections be kept on file, with a record of actions undertaken to comply with recommendations.

8. A description of the role of the dietetic department in the hospital's internal and external disaster plans.

9. Menus.

10. The role of the dietetic department in the preparation, storage, distribution and administration of enteric feeding, tube feeding and total parenteral nutrition programs.

11. Alterations in diets or diet schedules, including the provision of food service to patients who do not receive regular meal service.

12. Ancillary dietetic services, as appropriate, including food storage and kitchens on patient care units, formula supply, cafeterias, vending operations and ice making.

13. Personal hygiene and health of dietetic personnel.

14. A description of dietetic department policies and procedures designed to provide for infection control including a monitoring system to assure that dietetic personnel are free from communicable infections and open skin lesions.

15. A description of the identification system used for patient trays and other methods for assuring that each patient receives the appropriate diet as ordered.

16. Safety practices, including the control of electrical, flammable, mechanical, and as appropriate, radiation hazards.

17. Compliance with Chapter 64E-11, F.A.C.

(j) The dietetic department shall be designed and equipped to facilitate the safe, sanitary, and timely provision of food service to meet the nutritional needs of patients.

(k) The dietetic department shall have adequate equipment and facilities to prepare and distribute food, protect food from contamination and spoilage, to store foods under sanitary and secure conditions, and to provide adequate lighting, ventilation and humidity control.

(l) The dietetic department shall thoroughly cleanse and sanitize food contact surfaces, utensils, dishes and equipment between periods of use, shall ensure that adequate toilet, hand-washing and hand-drying facilities are conveniently available, and provide for adequate dishwashing and utensil washing equipment that prevent recontamination and are apart from food preparation areas.

(m) The dietetic department shall ensure that all walk-in refrigerators and freezers can be opened from inside and that all food and nonfood supplies are clearly labeled. Where stored in the same refrigerator, all nonfood supplies and specimens shall be stored on separate shelves from food supplies.

(n) The dietetic department shall implement methods to prevent contamination in the making, storage, and dispensing of ice.

(o) The dietetic department shall ensure that disposable containers and utensils are discarded after one use, and that worn or damaged dishes and glassware are discarded.

(p) The dietetic department shall hold, transfer, and dispose of garbage in a manner which does not create a nuisance or breeding place for pests or otherwise permit the transmission of disease.

(q) All matters pertaining to food service shall comply with Chapter 64E-11, F.A.C. Information on specifications, operation and maintenance of all major and fixed dietetic department equipment shall be maintained. A preventive and corrective maintenance program on such equipment shall be conducted and recorded.

(r) Dietetic services shall be provided in accordance with written orders by the individual responsible for the patient and appropriate information shall be recorded in the patient’s medical record. Such information shall include:

1. A summary of the dietary history and a nutritional assessment when the past dietary pattern is known to have a bearing on the patient’s condition;

2. Timely and periodic assessments of the patient’s nutrient intake and tolerance to the prescribed diet modification, including the effect of the patient’s appetite and food habits on food intake and any substitutions made;

3. A description or copy of diet information forwarded to another organization when a patient is discharged.

(s) Within 24 hours of admission and within 24 hours of any subsequent orders for diet modification, the diet order shall be confirmed by the practitioner responsible for the patient receiving oral alimentation.

(t) Each hospital shall establish appropriate quality control mechanisms to assure that:

1. All menus are evaluated for nutritional adequacy.

2. There is a means for identifying those patients who are not receiving oral intake.

3. Special diets are monitored.

4. The nutritional intake of patients is assessed and recorded as appropriate.

5. Effort is made to assure appetizing appearance, palatability, proper serving temperature, and retention of nutritional value of food.

6. Whenever possible, patient food preferences are respected and appropriate dietary substitutions are made available.

7. Surveys of patient acceptance of food are conducted, particularly for long-stay patients.

(2) Pharmacy. Each hospital shall develop and monitor procedures to assure the proper use of medications. Such procedures shall address prescription and ordering, preparation and dispensing, administration, and patient monitoring for medication effects. For purposes of providing medication services, each Class I and Class II hospital shall have on the premises, and each Class III hospital shall have on the premises or by contract, a pharmacy, pharmaceutical department or service, or similarly titled unit, and, when applicable, shall present evidence that it holds a current institutional or community pharmacy permit under the provisions of the Florida Pharmacy Act, Chapter 465, F.S.

(a) Each hospital shall maintain a hospital formulary or drug list which is developed and maintained by appropriate hospital staff, which shall be regularly updated. The formulary shall include the availability of non-legend medications, but does not preclude the use of unlisted drugs. Where unlisted drugs are used, there shall be a written policy and procedure for their prescription and procurement. Selection of medications for inclusion on the formulary shall be based on need, effectiveness, risks, and costs.

(b) Each hospital shall ensure that individuals who prescribe or order medications are legally authorized through the granting of clinical privileges.

(c) All drugs shall be prepared and stored under proper conditions of sanitation, temperature, light, moisture, ventilation, security and segregation to promote patient safety and proper utilization and efficacy.

(d) All medications shall be appropriately labeled as to applicable accessory or cautionary statements and their expiration date, shall be dispensed in as ready-to-administer forms as possible, and in quantities consistent with the patient’s needs which are designed to ensure minimization of errors and diversion.

(e) The pharmacist shall review each order before dispensing the medication, with the exception of situations in which a licensed independent practitioner with appropriate clinical privileges controls prescription ordering, preparation and administration of medicine. The pharmacist shall verify the order with the prescriber when there is a question.

(f) All medications shall be prepared and dispensed consistent with applicable law and rules governing professional licensure and pharmacy operation and in accordance with professional standards of pharmacy practice.

(g) A medication profile shall be developed and maintained by the pharmacy department for each patient and shall be available to staff responsible for the patient’s care. The medication profile shall include at least the name, birth date, sex, pertinent health problems and diagnoses, current medication therapy, medication allergies or sensitivities, and potential drug or food interactions.

(h) The hospital shall develop and implement a process for providing medications when the pharmacy is closed that ensures adequate control, accountability, and the appropriate use of medications.

(i) The hospital shall ensure there is an adequate and proper supply of emergency drugs within the pharmacy and in designated areas of the hospital.

(j) Receipt, distribution and administration of controlled drugs are documented by the pharmacy, nursing service and other personnel, to ensure adequate control and accountability in accordance with state and federal law.

(k) The hospital shall ensure that the administration of drugs shall take place in accordance with written policies, approved by the professional staff and designed to ensure that all medications are administered safely and efficiently.

(l) Each hospital’s pharmacy shall be directed by a licensed pharmacist, who may supervise satellite pharmacies, and who may be hired on a contract basis. The director of the hospital pharmacy, or other licensed pharmacists who are properly designated, shall be available to the hospital at all times, whether on duty or on call.

(m) Administration of drugs shall be undertaken only upon the orders of authorized members of the professional staff, where the orders are verified before administration, the patient is identified, and the dosage and medication is noted in the patient’s chart or medical record.

(n) Investigational medications shall be used only in accordance with specific hospital policy which addresses:

1. Review and approval of hospital participation in investigational studies by the appropriate hospital committee;

2. Requirements for informed consent by the patient;

3. Administration in accordance with an approved protocol;

4. Administration by personnel approved by the principal investigator after they have received information and demonstrated an understanding of the basic pharmacologic information about the medications; and

5. Documentation of doses dispensed, administered and destroyed.

(o) Each hospital shall have a system for the ongoing monitoring of each patient for medication effectiveness and actual or potential adverse effects or toxicity which includes:

1. A collaborative assessment of the effect of the medication on the patient based on observation and information gathered and maintained in the patient’s medical record and medication profile;

2. A process for the definition, identification, and review of significant medication errors and adverse drug reactions are reported in a timely manner in accordance with written procedures. Significant adverse drug reactions shall be reported promptly to the Food and Drug Administration;

3. Information from the medication monitoring is used to assess the continued administration of the medication;

4. Conclusions and findings of the medication monitoring are communicated to the appropriate health care personnel involved in the patient’s care.

(p) Each hospital shall have written policies and procedures governing the selection, procurement, distribution, administration, and record-keeping of all drugs, including provision for maintaining patient confidentiality. The policies and procedures shall be reviewed at least annually, dated to indicate time of last review, revised as necessary, and enforced.

(q) Parenteral nutrition services, when provided, shall be designed, implemented, and maintained to address assessment and reassessment of the patient, initial ordering and ongoing maintenance of medication orders, preparation and dispensing, administration, and assessing the effects on the patient.

(3) Surgical Department. Each Class I and Class II hospital, and each Class III hospital providing operative and other invasive procedures, shall be organized under written policies and procedures regarding surgical privileges, maintenance of the operating rooms, and evaluation and recording of treatment of the patient. All surgical department policies and procedures shall be available to the AHCA, shall be reviewed annually, dated to indicate time of last review, revised as necessary, and enforced. These procedures shall require:

(a) The determination of the appropriateness of the procedure for a patient to be based on:

1. The patient’s medical, anesthetic, and drug history;

2. The patient’s physical status;

3. Diagnostic data;

4. The risks and benefits of the procedure; and

5. The need to administer blood or blood components.

(b) The risks and benefits of the procedure are discussed with the patient prior to documenting informed consent and includes alternative options, if they exist, the need and risk of blood transfusions and available alternatives, and anesthesia options and risks.

(c) A preanesthesia evaluation of the patient shall be performed prior to surgery, except in the case of extreme emergency.

(d) Plans of care for the patient are formulated and documented in the medical record prior to the performance of surgery and shall include a plan for anesthesia, nursing care, the operative or invasive procedure, and the level of post-procedure care.

(e) The measurement of the patient’s physiological status is assessed during the administration of anesthesia and the surgical procedure.

(f) The post-procedure status of the patient is assessed on admission to the recovery area and prior to discharge from the recovery area.

(g) The patient is discharged by a qualified practitioner.

(h) Each hospital’s surgical department shall be organized functionally and physically as a distinct entity within the hospital. The operating room and accessory services shall be located in a manner to prevent through traffic, control traffic in and out, and maximize infection control.

(i) Each hospital shall designate a physician as medical advisor to the surgical department and a registered nurse to direct nursing services within the operating rooms of a surgical department.

(j) Each hospital shall document that all surgical nursing staff have received at least annual continuing education in safety, infection control and cardiopulmonary resuscitation.

(k) Each hospital shall maintain a roster of physicians specifying the surgical privileges of each, shall review the roster annually and revise it as necessary.

(l) A roster of “on-call” surgeons shall be promptly available at the operating room nursing stations.

(m) Each hospital’s surgical department shall maintain a record on a current basis that contains at least the following information:

1. Patient’s name;

2. Hospital number;

3. Preoperative diagnosis;

4. Post-operative diagnosis;

5. Procedure;

6. Names of surgeon, first assistant, and anesthetist;

7. Type of anesthetic; and

8. Complications, if any.

(n) Regardless of whether surgery is classified as major or minor, each hospital shall ensure, prior to any surgery being performed, except in emergency situations:

1. That there is a complete history and physical workup in the chart of every patient or, if such has been transcribed, but not yet recorded in the patient’s chart, that there is a statement to that effect and an admission noted by the physician in the chart; and

2. That there is evidence of informed consent for the operation in the patient’s chart.

(o) Each hospital shall ensure that immediately following each surgery, there is an operative report describing techniques and findings that is written or dictated and signed by the surgeon.

(p) The following minimum equipment shall be in each operating room suite:

1. Call-in system;

2. Oxygen, and means of administration;

3. Mechanical ventilatory assistance equipment, including airways, manual breathing bag, and ventilator and respirator;

4. Cardiac defibrillator with synchronization capability;

5. Respiratory and cardiac monitoring equipment;

6. Thoracentesis and closed thoracostomy sets;

7. Tracheostomy set, tourniquets, vascular cutdown sets, infusion pumps, laryngoscopes and endotracheal tubes;

8. Tracheobronchial and gastric suction equipment; and

9. A portable x-ray which shall be available, but need not be physically present in the operating suite.

(q) All infections of clean surgical cases shall be recorded and reported to the appropriate infections control authority, and a procedure shall exist for the investigation of such cases.

(r) A roster of “on-call” surgeons shall be promptly available at the operating room nursing stations.

(s) An on-call surgeon must be promptly available to the hospital when a call for services has been placed.

(4) Anesthesia Department. Each Class I and Class II hospital, and each Class III hospital providing surgical or obstetrical services, shall have an anesthesia department, service or similarly titled unit directed by a physician member of the organized professional staff.

(a) The anesthesia department of each hospital shall have written policies and procedures that are approved by the organized medical staff, are reviewed annually, dated at time of last review, revised, and enforced as necessary. Such written policies and procedures shall include at least the following requirements:

1. A preanesthesia evaluation of the patient by the physician, or qualified oral surgeon in the case of patients without medical problems admitted for dental procedures, or certified registered nurse anesthetist where authorized by established protocol approved by the medical staff, except in the case of emergencies.

2. A review of the patient’s condition immediately prior to induction of anesthesia.

3. A mechanism for release of patients from postanesthesia care.

4. A recording of all pertinent events taking place during the induction of, maintenance of, and emergence from anesthesia.

5. Guidelines for the safe use of all general anesthetic agents used in the hospital.

(b) The responsibilities and qualifications of all anesthesia personnel, including physician, nurse and dentist anesthetists and all trainees, must be defined in a policy statement, job description, or other appropriate document.

(c) Anesthetic safety regulations shall be developed, posted, and enforced. Such regulations shall include at least the following:

1. A requirement that all operating room electrical and anesthesia equipment be inspected on no less than a semi-annual basis, and that a written record of the results and corrective action be maintained.

2. A requirement that flammable anesthetic agents be employed only in areas in which a conductive pathway can be maintained between the patient and a conductive floor.

3. A requirement that each anesthetic gas machine have a pin-index or equivalent safety system.

4. A requirement that all reusable anesthesia equipment coming in direct contact with the patient be cleaned or sterilized in the manner prescribed by current medical standards.

(5) Nursing Service. Each hospital shall be organized and staffed to provide quality nursing care to each patient. Where a hospital’s organizational structure does not have a nursing department or service, it shall document the organizational steps it has taken to assure that oversight of the quality of nursing care provided to each patient is accomplished.

(a) Each hospital shall document the relationship of the nursing department to other units of the hospital by an organizational chart, and each nursing department shall have a written organizational plan that delineates lines of authority, accountability and communication. The nursing department shall assure that the following nursing management functions are fulfilled:

1. Review and approval of policies and procedures that relate to qualifications and employment of nurses.

2. Establishment of standards for nursing care and mechanisms for evaluating such care.

3. Implementing approved policies of the nursing department.

4. Assuring that a written evaluation is made of the performance of registered nurses and ancillary nursing personnel at the end of any probationary period and at a defined interval thereafter.

5. Each hospital shall employ a registered nurse on a full time basis who shall have the authority and responsibility for managing nursing services and taking all reasonable steps to assure that a uniformly optimal level of nursing care is provided throughout the hospital.

(b) The registered nurse shall be responsible for ensuring that a review and evaluation of the quality and appropriateness of nursing care is accomplished. The review and evaluation shall be based on written criteria, shall be performed at least quarterly, and shall examine the provision of nursing care and its effect on patients.

(c) The registered nurse shall ensure that education and training programs for nursing personnel are available and are designed to augment nurses’ knowledge of pertinent new developments in patient care and maintain current competence. Cardiopulmonary resuscitation training shall be conducted as often as necessary, but not less than annually, for all nursing staff members who cannot otherwise document their competence.

(d) Each hospital shall develop written standards of nursing practice and related policies and procedures to define and describe the scope and conduct of patient care provided by the nursing staff. These policies and procedures shall be reviewed at least annually, revised as necessary, dated to indicate the time of the last review, signed by the responsible reviewing authority, and enforced.

(e) The nursing process of assessment, planning, intervention and evaluation shall be documented for each hospitalized patient from admission through discharge.

1. Each patient’s nursing needs shall be assessed by a registered nurse at the time of admission or within the period established by each facility’s policy.

2. Nursing goals shall be consistent with the therapy prescribed by the responsible medical practitioner.

3. Nursing intervention and patient response, and patient status on discharge from the hospital, must be noted on the medical record.

(f) A sufficient number of qualified registered nurses shall be on duty at all times to give patients the nursing care that requires the judgment and specialized skills of a registered nurse, and shall be sufficient to ensure immediate availability of a registered nurse for bedside care of any patient when needed, to assure prompt recognition of an untoward change in a patient’s condition, and to facilitate appropriate intervention by nursing, medical or other hospital staff members.

(g) Each Class I and Class II hospital shall have at least one licensed registered nurse on duty at all times on each floor or similarly titled part of the hospital for rendering patient care services.

(h) Each hospital shall maintain a list of licensed personnel, including private duty and per diem nurses, with each individual’s current license number, and documentation of the nurses’ hours of employment, and unit of employment within the hospital.

(6) Housekeeping Services. Each hospital shall have an organized housekeeping department with a qualified person designated as responsible for all housekeeping functions. The designated supervisor of housekeeping shall be responsible for developing written policies and procedures for coordinating housekeeping services with other departments, developing a work plan and assignments for housekeeping staff, and developing a plan for obtaining relief housekeeping personnel.

(a) Each hospital shall employ a sufficient number of housekeeping personnel to fulfill the responsibilities of the housekeeping department seven days a week.

(b) When housekeeping services are provided by a third party, the hospital shall have a formal written agreement with the third party provider on file.

(c) Each hospital shall develop, implement, and maintain an effective housekeeping plan to ensure that the facility is maintained in compliance with the following:

1. The facility and its contents shall be kept free from dust, dirt, debris, and noxious odors;

2. All rooms and corridors shall be maintained in a clean, safe, and orderly condition, and shall be properly ventilated to prevent condensation, mold growth, and noxious odors;

3. All walls and ceilings, including doors, windows, skylights, screens, and similar closures shall be kept clean;

4. All mattresses, pillows, and other bedding; window coverings, including curtains, blinds, and shades, cubicle curtains and privacy screens; and furniture shall be kept clean;

5. Floors shall be kept clean and free from spillage, and non-skid wax shall be used on all waxed floors;

6. Articles in storage shall be elevated from the floor;

7. Aisles in storage areas shall be kept unobstructed;

8. All garbage and refuse from patient areas shall be collected daily and stored in a manner to make it inaccessible to insects and rodents;

9. Garbage or refuse storage rooms, if used, shall be kept clean, shall be vermin-proof, and shall be large enough to store the garbage and refuse containers that accumulate. Outside garbage or refuse storage areas or enclosures shall be large enough to store the garbage and refuse containers that accumulate, and shall be kept clean. Outside storage of unprotected plastic bags, wet strength paper bags, or baled units containing garbage or refuse is prohibited. Garbage and refuse containers, dumpsters, and compactor systems located outside shall be stored on or above a smooth surface of non-absorbent material, such as concrete or machine-laid asphalt, that is kept clean and maintained in good repair; and

10. Garbage and refuse shall be removed from both interior and outside storage areas as often as necessary to prevent sanitary nuisance conditions. If garbage and refuse are disposed of on the facility premises, the method of disposal shall not create a sanitary nuisance and shall comply with the provisions of Chapter 17-7, F.A.C.

(d) Each hospital shall ensure that:

1. There is a sufficient quantity of linen, including at least sheets, pillow cases, drawsheets or their alternative, blankets, towels and washcloths to provide comfortable, clean and sanitary conditions for each patient at all times;

2. Written policies and procedures for linen and laundry services, including methods of collection, storage, and transportation are developed, implemented, and maintained in conjunction with the policies and procedures developed by the infection control committee;

3. Soiled linen and laundry are collected in a way that minimizes microbial dissemination into the environment;

4. Separate containers are used for transporting clean linen and laundry, and soiled linen and laundry;

5. Soiled linen and laundry are stored in a ventilated area separate from any other supplies, and are not stored, sorted, rinsed, or laundered in patient rooms, bathrooms, areas of food preparation or storage, or areas in which clean material and equipment are stored; and

6. When linen and laundry services are provided by a third party, the third party provider shall be required to maintain at least the standards contained herein, and shall ensure that clean linen is packaged and protected from contamination until received by the facility.

(e) Effective control methods shall be employed to protect against the entrance into the facility and the breeding or presence on the premises of flies, roaches, rodents, and other vermin. Use of pesticides shall be in accordance with Chapter 5E-14, Part No. 1, F.A.C.

(f) Each hospital shall develop and implement, in coordination with the infection control committee, written procedures for the cleaning of the physical plant, equipment, and reusable supplies. Such procedures shall include:

1. Special written procedures for cleaning all infectious disease areas;

2. Special written procedures for cleaning all operating room suites, delivery suites, nurseries, intensive and other critical care units, the emergency suite, and other areas performing similar functions; and

3. Special written procedures for the separate handling and storage of both clean and dirty linen, with special attention being given to identification, separation and handling of linens from isolation or infectious disease areas.

(7) Ambulatory Care Services. Each hospital offering ambulatory care services under it’s hospital license shall establish policies and procedures to ensure that quality care based on the needs of the patient will be delivered at all times.

(a) Ambulatory care services shall be under the direction of a licensed physician(s) responsible for the clinical direction of patient care and treatment services, and whose qualifications, authority, and responsibilities are defined in writing as approved by the governing body.

(b) Ambulatory care services shall be staffed with appropriately trained and qualified individuals to provide the scope of services anticipated to meet the needs of the patients.

(c) Each patient’s general medical condition shall be managed by a physician with appropriate clinical privileges, as determined by medical staff bylaws.

(d) When any ambulatory care services are provided by non-hospital employees, the provider shall meet all safety requirements, abide by all pertinent rules and regulations of the hospital and medical staff, and document the quality improvement measures to be implemented.

(e) The provisions of ambulatory nursing care shall be supervised by a registered nurse who is qualified by relevant training and experience in ambulatory care.

(f) Sufficient personnel shall be on duty to provide efficient and effective patient care services.

(g) The scope of services offered, and the relationship of the ambulatory services program to other hospital units, as well as all supervisory relationships within the program, shall be defined in writing, and must be provided in accordance with the standards set by the governing body’s bylaws and the rules and regulations of the medical staff.

(h) Written policies and procedures to guide the operation of the ambulatory services program shall be developed, reviewed, and revised as necessary, dated to indicate the time of last revision, and enforced.

(i) A medical record must be maintained on every patient who receives ambulatory care services. Medical records shall be managed and maintained in accordance with acceptable professional standards and practices. Confidentiality and disclosure of patient information contained in the health record must be maintained in accordance with hospital policy and state and federal law. Each patient’s medical record must include at a minimum, the following information, and be updated as necessary:

1. Patient identification;

2. Relevant history of the illness or injury and of physical findings;

3. Diagnostic and therapeutic orders;

4. Clinical observations, including the results of treatment;

5. Reports of procedures and tests, and their results;

6. Diagnosis or impression;

7. Allergies;

8. Referrals to practitioners or providers of services internal or external to the hospital;

9. Communications to and from practitioners or providers of service external to the hospital;

10. Growth charts for children and adolescents as needed when the service is the source of primary care; and

11. Immunization status of children and adolescents and others as determined by law and/or hospital policy.

(j) To facilitate the ongoing provision of care, a problem list of known significant diagnoses, conditions, procedures, drug allergies and medications shall be maintained for each patient who receives ambulatory services. The problem list shall be initiated no later than the third visit and include items based on any initial medical history and physical examination, and updated on subsequent visits with additional information as necessary. The problem list shall include at least the following items:

1. Known significant medical diagnoses and conditions;

2. Known significant surgical and invasive procedures;

3. Known adverse and allergic reactions to drugs; and

4. Medications known to be prescribed for and/or used by the patient.

(8) Obstetrical Department. If provided, obstetrical services shall include labor, delivery, and nursery facilities, and be formally organized and operated to provide complete and effective care for each patient.

(a) Except in hospitals licensed for 75 beds or less, the obstetrical service shall be separated from other patient care rooms and shall have separate nursing staff. When obstetrical services are provided in hospitals of 75 beds or less, there shall be:

1. A written and enforced policy concerning the placement of obstetrical patients in a manner most conducive to meet their special needs, and

2. A demonstration by the hospital that its nursing staff possesses specialized skills in obstetrics and pediatrics, whether by training or by obstetrical experience, and can provide service to obstetrical patients and their infants on a 24 hour basis, whether on duty, on call, or on a consultative basis.

(b) In those hospitals with a formally organized obstetrical department, clean gynecological and surgical patients may be admitted to the unit under specific written controls approved by the medical staff and governing authority when there is a written demonstrated need in each case.

(c) Every infant born in a hospital shall be properly identified immediately at the time of birth. Identification of the infant shall be done in the delivery room, birthing room, or other place of birth within the hospital, before either the mother or the infant is transferred to another part of the facility.

(9) Laboratories and Pathology Services. Clinical Laboratory–Every hospital must provide on the premises or by contract with a laboratory licensed under Chapter 483, Part I, F.S., a clinical laboratory to provide those services commensurate with the hospital’s needs and which conforms to the provisions of Chapter 483, Part I, F.S., and Chapter 59A-7, F.A.C.

(a) Provisions shall be made to carry out clinical laboratory examinations, including routine chemistry, microbiology, hematology, general immunology, and urinalysis.

(b) Provision shall be made for assuring the availability of emergency laboratory services. Such services shall be available 24 hours a day, seven days a week, including holidays.

(c) Reports of all examinations shall be filed with the patient’s record.

(d) Pathology Laboratory–Each hospital shall provide on the premises or by contract with a laboratory licensed under Chapter 483, Part I, F.S., pathology laboratory services commensurate with hospital’s needs and which conforms with the provisions of Chapter 483, Part I, F.S., and Chapter 59A-7, F.A.C.

(e) All specimens removed in operations shall be sent to a pathologist for examination, except when another suitable means of verification of removal is routinely employed, when there is an authenticated report to document the removal, and when quality of care will not be compromised by the exception. Hospitals may establish a policy for excepting certain categories of specimens from examination when it determines quality of care will not be compromised or examination will yield no useful information. Signed reports on all specimens removed in an operation, whether documented by a pathologist or through an alternative means, shall be filed with the patient’s record.

(f) If the hospital does not maintain a pathology laboratory there shall be policy established and enforced, which meets the provisions of paragraph (a).

(g) Blood Bank Services–Each hospital shall either maintain on the premises, or by contract have convenient access to, a blood banking service which is under the control and supervision of a pathologist or other authorized physician to perform those services commensurate with the facility’s needs, and ensure that the laboratory is licensed under the provisions of Chapter 483, Part I, F.S., and Chapter 59A-7, F.A.C.

(h) Records shall be kept on file indicating the receipt and disposition of all blood provided to patients in the facility.

(i) All Class I and Class II hospitals, and all Class III hospitals utilizing blood and blood by-products, shall:

1. Maintain facilities for procurement, safekeeping and transfusion of blood and blood products, or have them readily available;

2. Maintain a temperature alarm system for blood storage facilities, where applicable, which is tested and inspected quarterly and is otherwise safe.

3. The alarm system must be audible, and must monitor proper blood and blood product storage temperature over a 24-hour period.

4. Tests of the alarm system must be documented.

5. If blood is stored or maintained for transfusion outside of a monitored refrigerator, the laboratory must ensure and document that storage conditions, including temperature, are appropriate to prevent deterioration of the blood or blood product.

6. Promptly dispose of blood which has exceeded its expiration date.

(j) Class III hospitals not utilizing blood and blood by-products need not maintain blood storage facilities.

(10) Radiology Services. Each Class I and Class II hospital shall provide on the premises, and each Class III hospital shall provide on the premises or by contract, diagnostic imaging facilities according to the needs of the hospital and conform to Chapter 404, F.S., Chapter 64E-5, F.A.C., Part IV, Chapter 468, F.S., and Chapter 64E-3, F.A.C.

(a) The radiology department or other similarly titled part shall be maintained free of hazards for patients and personnel.

(b) Each hospital shall have a radiologist either full time or part time on a consulting basis to discharge professional radiology services.

(c) Each hospital shall have certified radiologic technologists or basic x-ray machine operator in hospitals of 150 beds or less, and shall be on duty or on call at all times, pursuant to Part IV, Chapter 468, F.S.; and Chapter 64E-3, F.A.C.

(d) The use of all diagnostic imaging apparatus shall be limited to personnel designated as specified in Part IV, Chapter 468, F.S., and Chapter 64E-3, F.A.C.

(e) The credentials of each person providing diagnostic and therapeutic radiation, imaging and nuclear medicine services, including formal training, on-the-job experience, and certification or licensure where applicable, shall be maintained on file at all times.

(f) Each hospital shall maintain and enforce policies and procedures for the provision of all diagnostic and therapeutic radiation, imaging, and nuclear medicine services, and ensure compliance with the requirements of Chapter 64E-5, F.A.C. Such policies and procedures shall be written, reviewed annually, and revised as necessary in conformance with Chapter 64E-5, F.A.C., and shall be dated as to time of last review.

(g) Each hospital shall require that all diagnostic and therapeutic radiology, imaging or nuclear medicine services be performed only upon written order of a licensed physician. The request and all results must be recorded in the patient’s medical record;

(h) Each hospital shall ensure documentation, and reporting to the Bureau of Radiation Control of the Department of Health of all misadministration of radioactive materials, as those terms are defined by Chapter 64E-5, F.A.C.

(i) Each hospital shall maintain and document in writing a quality control program designed to minimize the unnecessary duplication of radiographic studies, to minimize exposure time of patients and personnel, and to maximize the quality of diagnostic information and therapy provided.

(11) Respiratory Therapy. Each hospital shall have written policies and procedures describing the scope of diagnostic and therapeutic respiratory services provided to patients of the hospital. This document shall contain written guidelines for the transfer or referral of patients requiring respiratory care services not provided at the hospital.

(a) When respiratory care services are provided outside the hospital, the hospital shall ensure by contract or other enforceable mechanism that such services meet all safety requirements and quality control measures required by the hospital.

(b) Respiratory care services provided within a hospital shall have medical direction provided by a physician member of the organized medical staff with special interest and knowledge in the management of acute and chronic respiratory problems. The physician director shall be responsible for the overall direction of respiratory services, for conducting a review of the quality, safety and appropriateness of respiratory care services at least quarterly, and shall be available for any required respiratory care consultation.

(c) Respiratory care services in a hospital may be supervised by a technical director who is registered or certified by the National Board of Respiratory Care Inc., or has the documented equivalent education, training and experience. Other respiratory care personnel shall provide respiratory care commensurate with their documented training, experience, and competence.

(d) The formal training of respiratory therapy students shall be carried out only in programs accredited by appropriate professional educational organizations. Individuals in student status shall be directly supervised when engaged in patient care activities.

(e) The education, training and experience of personnel who provide respiratory care services shall be documented, and shall be related to each individual’s level of participation in the provision of respiratory care services.

(f) Nonphysician respiratory care personnel shall not perform patient procedures associated with a potential hazard, including arterial puncture for obtaining blood samples, unless authorized in writing by the physician director of the respiratory care service acting in accordance with professional staff policy.

(g) All personnel providing respiratory care services shall participate in relevant in-service education programs. Such participation shall occur at least annually, and shall include instruction in safety, infection control, and cardiopulmonary resuscitation, except for individuals who can otherwise demonstrate their competence.

(h) There shall be written policies and procedures specifying the scope and conduct of patient care rendered in the provision of respiratory care services. All policies and procedures must be approved by the physician director, reviewed at least annually, revised as necessary, dated to indicate the time of last review, and enforced. Respiratory care policies shall include at least the following:

1. Specification as to who may perform specific procedures and provide instruction, under what circumstances, and under what degree of supervision.

2. Assembly and sequential operation of equipment and accessories to implement therapeutic regimes.

3. Steps to be taken in the event of adverse reactions, and other emergencies.

4. Procurement, handling, storage and dispensing of therapeutic gases.

5. Infection control measures, including specifics as to changing and cleansing of equipment.

6. Administration of medications in accordance with the physician’s order.

(i) The respiratory care service shall have sufficient equipment and facilities to assure the safe, effective and timely provision of respiratory care service to patients.

1. All equipment shall be calibrated and operated according to manufacturer’s specifications, and shall be periodically inspected and maintained.

2. Where piped-in gas is used, an evaluation shall be made prior to use to assure identification of the gas and its delivery within an established safe pressure range.

3. Ventilators used for continuous assistance or controlled breathing shall have operative alarm systems at all times.

(j) Prescriptions for respiratory care shall specify the type, frequency and duration of treatment and, as appropriate, the type and dose of medication, the type of dilutent, and the oxygen concentration, and shall be incorporated into the patient’s medical record.

(12) Special Care Units. The hospital shall ensure that a special care unit is a physically and functionally distinct entity within the hospital, has controlled access, and has an effective means of isolation for patients suffering from communicable or infectious disease or acute mental disorder. Special care units shall provide:

(a) Direct or indirect visual observation by unit staff of all patients from one or more vantage points;

(b) A direct intercommunication or alarm system between the nurse’s station and the bedside; and

(c) Beds that are adjustable to positions required by the patient, that are easily movable, and that have a locking or stabilizing mechanism to attain a secure, stationary position. Headboards, when present, shall be removable or adjustable to permit ready access to the patient’s head.

(d) Each special care unit shall be advised by a physician who is a member of the organized medical staff, shall have its relationship to other departments and units of the hospital specified in writing (organizational chart), and shall provide relevant in-service education programs to all staff including, but not limited to, annual education concerning cardiopulmonary resuscitation and safety and infection control requirements.

(e) Written policies and procedures shall be developed concerning the scope and provision of care in each special care unit. Such policies and procedures shall be reviewed at least annually, revised as necessary, dated to indicate the time of last review, enforced, and include at least the following:

1. Specific criteria for the admission and discharge of patients;

2. A system for informing the responsible physician of changes in the patient's condition;

3. Methods for procurement of equipment and drugs at all times;

4. Specific procedures relating to infection and traffic control;

5. Specification as to who may perform special procedures, under what circumstances, and under what degree of supervision; and specific policies as to the use of standing orders; and

6. A protocol for handling emergency conditions related to the breakdown of essential equipment.

(f) No hospital shall hold itself out as a Trauma Center unless it has been verified by the Department of Health and Rehabilitative Services in accordance with the Trauma Center provisions of Section 395.401, F.S., and Chapter 10D-86, F.A.C. Any violation of the Trauma Center provisions shall subject any violator to appropriate remedies provided by Section 395.1065, F.S.

(13) Adult Diagnostic Cardiac Catheterization Program. All licensed hospitals that establish adult diagnostic cardiac catheterization laboratory services under Section 408.0361, F.S., shall operate in compliance with the guidelines of the American College of Cardiology/American Heart Association regarding the operation of diagnostic cardiac catheterization laboratories. Hospitals are considered to be in compliance with American College of Cardiology/American Heart Association guidelines when they adhere to standards regarding staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety. The applicable guideline, herein incorporated by reference, is the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 (American College of Cardiology/American Heart Association guidelines). Aspects of the guideline related to pediatric services or outpatient cardiac catheterization in freestanding non-hospital settings are not applicable to this rule. All such licensed hospitals shall have a department, service or other similarly titled unit which shall be organized, directed and staffed, and integrated with other units and departments of the hospitals in a manner designed to assure the provision of quality patient care.

(a) Licensure.

1. A hospital seeking a license for an adult diagnostic cardiac catheterization laboratory services program shall submit an application on a form provided by the Agency, AHCA Form 3130-5003, August 09, License Application  Adult Inpatient Diagnostic Cardiac Catheterization, incorporated herein by reference and available at http://ahca.myflorida.com/MCHQ/Health_Facility_Regulation/Hospital_Outpatient/hospital.shtml#acs, signed by the chief executive officer of the hospital, confirming the hospital’s intent and ability to comply with Section 408.0361(1), F.S.

2. Hospitals with adult diagnostic cardiac catheterization services programs must renew their licenses at the time of the hospital licensure renewal, providing the information in Section 408.0361(1), F.S. Failure to renew the hospital’s license or failure to update the information in Section 408.0361(1), F.S., shall cause the license to expire.

(b) Definitions. The following definitions shall apply specifically to all adult diagnostic cardiac catheterization programs, as described in this subsection 59A-3.2085(13), F.A.C.:

1. “Diagnostic Cardiac Catheterization” means a procedure requiring the passage of a catheter into one or more cardiac chambers of the left and right heart, with or without coronary arteriograms, for the purpose of diagnosing congenital or acquired cardiovascular diseases, or for determining measurement of blood pressure flow; and also includes the selective catheterization of the coronary ostia with injection of contrast medium into the coronary arteries.

2. “Adult” means a person fifteen years of age or older.

3. Therapeutic Procedures. An adult diagnostic cardiac catheterization program established pursuant to Section 408.0361, F.S., shall not provide therapeutic services, such as percutaneous coronary intervention or stent insertion, intended to treat an identified condition or the administering of intra-coronary drugs, such as thrombolytic agents.

4. Diagnostic Procedures. Procedures performed in the adult diagnostic cardiac catheterization laboratory shall include, for example, the following:

a. Left heart catheterization with coronary angiography and left ventriculography;

b. Right heart catheterization;

c. Hemodynamic monitoring line insertion;

d. Aortogram;

e. Emergency temporary pacemaker insertion;

f. Myocardial biopsy;

g. Diagnostic trans-septal procedures;

h. Intra-coronary ultrasound (CVIS);

i. Fluoroscopy; and

j. Hemodynamic stress testing.

(c) Support Equipment. A crash cart containing the necessary medication and equipment for ventilatory support shall be located in each cardiac catheterization procedure room. A listing of all crash cart contents shall be readily available. At the beginning of each shift, the crash cart shall be checked for intact lock; the defribrillator and corresponding equipment shall be checked for function and operational capacity. A log shall be maintained indicating review.

(d) Radiographic Cardiac Imaging Systems. A quality improvement program for radiographic imaging systems shall include measures of image quality, dynamic range and modulation transfer function. Documentation indicating the manner in which this requirement will be met shall be available for the Agency’s review.

(e) Physical Plant Requirements. Section 419.2.1.2, Florida Building Code, contains the physical plant requirements for the adult diagnostic cardiac catheterization program.

(f) Personnel Requirements. There shall be an adequate number of trained personnel available. At a minimum, a team involved in cardiac catheterization shall consist of a physician, one registered nurse, and one technician.

(g) Quality Improvement Program. A quality improvement program for the adult diagnostic cardiac catheterization program laboratory shall include an assessment of proficiency in diagnostic coronary procedures, as described in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 guidelines. Essential data elements for the quality improvement program include the individual physician procedural volume and major complication rate; the institutional procedural complication rate; relevant clinical and demographic information about patients; verification of data accuracy; and procedures for patient, physician and staff confidentiality. Documentation indicating the manner in which this requirement will be met shall be available for the Agency’s review.

(h) Emergency Services.

1. All providers of adult diagnostic cardiac catheterization program services in a hospital not licensed as a Level II adult cardiovascular services provider shall have written transfer agreements developed specifically for diagnostic cardiac catheterization patients with one or more hospitals that operate a Level II adult cardiovascular services program. Written agreements must be in place to ensure safe and efficient emergency transfer of a patient within 60 minutes. Transfer time is defined as the number of minutes between the recognition of an emergency as noted in the hospital’s internal log and the patient’s arrival at the receiving hospital. Transfer and transport agreements must be reviewed and tested at least every 3 months, with appropriate documentation maintained, including the hospital’s internal log or emergency medical services data.

2. Patients at high risk for diagnostic catheterization complications shall be referred for diagnostic catheterization services to hospitals licensed as a Level II adult cardiovascular services provider. Hospitals not licensed as a Level II adult cardiovascular services provider must have documented patient selection and exclusion criteria and provision for identification of emergency situations requiring transfer to a hospital with a Level II adult cardiovascular services program. Documentation indicating the manner in which this requirement will be met shall be available for the Agency’s review.

(i) Policy and Procedure Manual for Medicaid and Charity Care.

1. Each provider of adult diagnostic cardiac catheterization services shall maintain a policy and procedure manual, available for review by the Agency, which documents a plan to provide services to Medicaid and charity care patients.

2. At a minimum, the policy and procedure manual shall document specific outreach programs directed at Medicaid and charity care patients for adult diagnostic cardiac catheterization services.

(j) Enforcement. Enforcement of these rules shall follow procedures established in Rule 59A-3.253, F.A.C.

(k) In case of conflict between the provisions of this rule and the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 guidelines, the provisions of this part shall prevail.

(14) Mobile Surgical Facility. A mobile surgical facility as defined in Section 395.002(21), F.S., provides elective surgical care under contract with the Department of Corrections or a private correctional facility operating pursuant to Chapter 957, F.S., and not to the general public. The mobile surgical facility shall comply with the provisions of this chapter, except as modified herein.

(a) Licensure Procedure. Each application for a mobile surgical facility license, or renewal thereof, shall be accompanied by a license fee of $1500.00. The agency shall issue a single license, which identifies the mobile surgical facility. This license is not transferable.

(b) Licensure Inspection. The agency shall inspect a mobile surgical facility at initial licensure pursuant to Section 395.0161(1)(f), F.S. This subsection shall only apply to mobile surgical facilities operating under contracts entered into on or after July 1, 1998.

(c) Governing Body. Each mobile surgical facility shall have its own governing body that assumes full responsibility for the legal and ethical conduct of the facility consistent with its contract with the Department of Corrections. The governing body is organized under approved written bylaws, rules and regulations, which are reviewed annually and updated as required.

(d) Organized Medical Staff. Each mobile surgical facility shall have an organized medical staff approved by the governing body in accordance with its contract with the Department of Corrections, with the delegated responsibility to provide for the quality of all medical care and other appropriate health care provided to patients, for planning for the improvement of that care, and for the ethical conduct and professional practices of its members.

(e) Services Provided. Each mobile surgical facility shall have written policies and procedures describing the scope of services provided to the inmate patients of the correctional facility. Services provided by the mobile surgical facility include but not limited to:

1. Surgical Services. The surgical service shall be organized under written policies and procedures relating to surgical staff privileges, anesthesia, function standards, staffing patterns and quality maintenance of the mobile surgical facility.

2. Anesthesia Services. The mobile surgical facility anesthesia services shall be organized under written policies and procedures relating to anesthesia staff privileges, the administration of anesthesia, and the maintenance of strict safety controls.

3. Nursing Services. The mobile surgical facility shall have written policies and procedures relating to patient care, establishment of standards for nursing care, and mechanisms for evaluating such care, and nursing services.

4. Laboratories. The mobile surgical facility shall provide on the premises or through arrangement with a laboratory licensed under Chapter 483, F.S., and Chapter 59A-7, F.A.C., a clinical laboratory to provide those services commensurate with the mobile surgical facility’s needs.

5. Radiological Services. The mobile surgical facility shall provide within the facility, or through arrangement, diagnostic radiological services commensurate with its needs.

6. Housekeeping Service. The mobile surgical facility housekeeping service shall be organized under effective written policies and procedures relating to personnel, equipment, materials, maintenance, and cleaning of all areas of the mobile surgical facility.

7. Surveillance, Prevention, and Control of Infection. Each mobile surgical facility shall establish an infection control program involving members of its medical staff, nursing staff, other professional and administrative staff as appropriate.

8. Patient Rights. The mobile surgical facility shall develop and adopt policies and procedures for the protection of patients rights pursuant to Sections 381.026, FS.

9. Medical Records. Each mobile surgical facility shall use a problem oriented medical record for each patient, which shall be initiated at the time of intake or admission and which shall contain all pertinent information pursuant to 59A-3.217, F.A.C.

10. Coordination of Care. Each mobile surgical facility shall develop and implement policies and procedures on discharge planning pursuant to Rule 59A-3.2055, F.A.C. Documentation of the discharge plan in the patient’s medical record shall include an assessment of appropriate services to meet the patient needs following surgery.

11. Quality Assessment and Improvement. The mobile surgical facility shall have an ongoing quality improvement system designed to objectively and systematically monitor and evaluate the quality and appropriateness of patient care and opportunities to improve the quality of care provided pursuant to Rule 59A-3.216, F.A.C.

12. Comprehensive Emergency Management Plan. The mobile surgical facility shall have a comprehensive emergency management plan for internal or external disasters. The comprehensive emergency management Plan shall be reviewed and approved by the county office of emergency management and updated annually as required.

(15) Stroke centers.

(a) Primary Stroke Centers. A hospital program will be designated as a primary stroke center on the basis of that hospital providing to the Agency for Health Care Administration an affidavit on AHCA Form 3130-8009, December 2005, which is incorporated by reference, signed by the Chief Executive Officer of the hospital, attesting that the program has been certified by the Joint Commission on Accreditation of Healthcare Organizations (JCAHO) as a primary stroke center, or that the program meets the criteria applicable to primary stroke centers as outlined in the Joint Commission on Accreditation of Healthcare Organizations: Disease-Specific Care Certification Manual, 2nd Edition, Oakbrook Terrace, IL; © Joint Commission Resources, 2005. Reprinted with permission. Attestation must also indicate that the program meets requirements outlined in the “Updated Primary Stroke Center Certification Appendix for the Disease-Specific Care Manual,” which are incorporated by reference. Copies of these standards are available from the Agency for Health Care Administration Hospital and Outpatient Services Unit, or from the Joint Commission on the Accreditation of Healthcare Organizations at One Renaissance Boulevard, Oak Terrace, IL 60181. Hospitals shall ensure that stroke centers establish specific procedures for screening patients that recognize that numerous conditions, including cardiac disorders, often mimic stroke in children. Stroke centers should ensure that transfer to an appropriate facility for specialized care is provided to children and young adults with known childhood diagnoses.

(b) Comprehensive Stroke Center (CSC). Hospitals shall ensure that stroke centers establish specific procedures for screening patients that recognize that numerous conditions, including cardiac disorders, often mimic stroke in children. Stroke centers should ensure that transfer to an appropriate facility for specialized care is provided to children and young adults with known childhood diagnoses. A hospital’s program may be designated as a Comprehensive Stroke Center on the basis of that hospital providing to the Agency for Health Care Administration an affidavit signed by the Chief Executive Officer of the hospital that the program has received initial Primary Stroke Center designation as provided in paragraph 59A-3.2085(15)(a), F.A.C., and that the program meets the following criteria:

1. A comprehensive stroke center shall have health care personnel with clinical expertise in a number of disciplines available.

a. Health care personnel disciplines in a CSC shall include:

(I) A designated comprehensive stroke center medical director;

(II) Neurologists, neurosurgeons, surgeons with expertise performing carotid endartrectomy, diagnostic neuroradiologist(s), and physician(s) with expertise in endovascular neuroInterventional procedures and other pertinent physicians;

(III) Emergency department (ED) physician(s) and nurses trained in the care of stroke patients;

(IV) Nursing staff in the stroke unit with particular neurologic expertise who are trained in the overall care of stroke patients;

(V) Nursing staff in intensive care unit (ICU) with specialized training in care of patients with complex and/or severe neurological/neurosurgical conditions;

(VI) Advanced Practice Nurse(s) with particular expertise in neurological and/or neurosurgical evaluation and treatment, physician(s) with specialized expertise in critical care for patients with severe and/or complex neurological/neurosurgical conditions;

(VII) Physician(s) with specialized expertise in critical care for patients with severe and/or complex neurological/neurosurgical conditions;

(VIII) Physician(s) with expertise in performing and interpreting trans-thoracic echocardiography, transesophageal echocardiography, carotid duplex ultrasound and transcranial Doppler;

(IX) Physician(s) and therapist(s) with training in rehabilitation, including physical, occupational and speech therapy; and

(X) A multidisciplinary team of health care professionals with expertise or experience in stroke, representing clinical or neuropsychology, nutrition services, pharmacy (including a Pharmacy Doctorate (Pharm D) with stroke expertise), case management and social workers.

b. Availability of medical personnel:

(I) Neurosurgical expertise must be available in a CSC on a 24 hours per day, 7 days per week basis and in-house within 2 hours. The attending neurosurgeon(s) at a CSC should have expertise in cerebrovascular surgery.

(II) Neurologist(s) with special expertise in the management of stroke patients should be available 24 hours per day, 7 days per week.

(III) Endovascular/Neurointerventionist(s) should be on active full-time staff. However, when this service is temporarily unavailable, pre-arranged transfer agreements must be in place for the rapid transfer of patients needing these treatments to an appropriate facility.

2. Advanced Diagnostic Capabilities.

a. Magnetic resonance imaging (MRI) and related technologies.

b. Catheter angiography.

c. Coaxial Tomography (CT) angiography.

d. Extracranial ultrasonography.

e. Carotid duplex.

f. Transcranial Doppler.

g. Transthoracic and trans-esophageal echocardiography.

h. Tests of cerebral blood flow and metabolism.

i. Comprehensive hematological and hypercoagulability profile testing.

3. Neurological Surgery and Endovascular Interventions.

a. Angioplasty and stenting of intracranial and extracranial arterial stenosis.

b. Endovascular therapy of acute stroke.

c. Endovascular treatment (coiling) of intracranial aneurysms.

d. Endovascular and surgical repair of arteriovenous malformations (AVM) and arteriovenous fistulae (AVF).

e. Surgical clipping of intracranial aneurysms.

f. Intracranial angioplasty for vasospasm.

g. Surgical resection of AVMs and AVFs.

h. Placement of ventriculostomies and ventriculoperitoneal shunts.

i. Evacuation of intracranial hematomas.

j. Carotid endarterectomy.

k. Decompressive craniectomy.

4. Specialized Infrastructure.

a. Emergency Medical Services (EMS) Link – The CSC collaborates with EMS leadership:

(I) To ensure that EMS assessment and management at the scene includes the use of a stroke triage assessment tool (consistent with the Florida Department of Health sample).

(II) To ensure that EMS assessment/management at the scene is consistent with evidence-based practice.

(III) To facilitate inter-facility transfers.

(IV) To maintain an on-going communication system with EMS providers regarding availability of services.

b. Referral and Triage – A CSC shall maintain:

(I) An acute stroke team available 24 hours per day, 7 days per week, including: ED physician(s), nurses for ED patients, neurologist, neurospecialist RNs, radiologist with additional staffing/technology including: 24 hours per day, 7 days per week CT availability, STAT lab testing/pharmacy and registration.

(II) A system for facilitating inter-facility transfers.

(III) Defined access telephone numbers in a system for accepting appropriate transfer.

c. Inpatient Units – These specialized units should have a subspecialty Medical Director with particular expertise in stroke (intensivist, pulmonologist, neurologist, neurosurgeon or neuro-intensivist) who demonstrates ongoing professional growth by obtaining at least 6 CME credits in cerebrovascular care annually.

(I) ICU with medical and nursing personnel who have special training, skills and knowledge in the management of patients with all forms of neurological/neurosurgical conditions that require intensive care.

(II) Acute Stroke Unit with medical and nursing personnel who have training, skills and knowledge sufficient to care for patients with neurological conditions, particularly acute stroke patients, and who are appropriately trained in neurological assessment and management.

d. Rehabilitation and Post Stroke Continuum of Care –

(I) A CSC shall provide inpatient post-stroke rehabilitation.

(II) A CSC shall utilize healthcare professionals who can assess and treat cognitive, behavioral, and emotional changes related to stroke (i.e., clinical psychologists or clinical neuropsychologists).

(III) A CSC shall ensure discharge planning that is appropriate to the level of post-acute care required.

(IV) A CSC shall ensure continuing arrangements post-discharge for rehabilitation needs and medical management.

(V) A CSC shall ensure that patients meeting acute care rehabilitation admission criteria are transferred to a CARF/JCAHO accredited acute rehabilitation facility.

e. Education –

(I) The CSC shall fulfill the educational needs of its medical and paramedical professionals by offering ongoing professional education for all disciplines.

(II) The CSC shall provide education to the public as well as to inpatients and families on risk factor reduction/management, primary and secondary prevention of stroke, the warning signs and symptoms of stroke, and the medical management and rehabilitation for stroke patients.

(III) The CSC shall supplement community resources for stroke and stroke support groups.

f. Professional standards for nursing – The CSC shall provide a career development track to develop neuroscience nursing, particularly in the area of cerebrovascular disease.

(I) ICU and neuroscience/stroke unit nursing staff will be familiar with stroke specific neurological assessment tools such as the National Institute for Health (NIH) Stroke Scale.

(II) ICU nursing staff must be trained to assess neurologic function and be trained to provide all aspects of neuro critical care.

(III) Nurses in the ICU caring for stroke patients, and nurses in neuroscience units must obtain at least 8 hours of continuing education credits (4 hours continuing education in the formalized CEU credits and 4 hours of continuing education related to their specialty that can be verified through documentation of participation).

g. Research – A CSC shall have the professional and administrative infrastructure necessary to conduct clinical trials and should have participated in stroke clinical trials within the last year and actively participate in ongoing clinical stroke trials.

5. Quality Improvement and Clinical Outcomes Measurement.

a. The purpose of a quality improvement program is analysis of data, correction of errors, systems improvements, and ongoing improvement in patient care and delivery of services.

b. A multidisciplinary institutional Quality Improvement Committee should meet on a regular basis to monitor quality benchmarks and review clinical complications.

c. Specific benchmarks, outcomes, and indicators should be defined, monitored, and reviewed on a regular basis for quality assurance purposes. Outcomes for procedures such as carotid endarterectomy, carotid stenting, IVtPA, endovascular/interventional stroke therapy, intracerebral aneurysm coiling, and intracerebral aneurysm clipping should be monitored.

d. A database and/or registry should be established that allows for tracking of parameters such as length of stay, treatments received, discharge destination and status, incidence of complications (such as aspiration pneumonia, urinary tract infection, deep venous thrombosis), and discharge medications and comparing to institutions across the United States.

e. A CSC shall participate in a national and/or state registry (or registries) for acute stroke therapy clinical outcomes, including IVtPA and endovascular/interventional stroke therapy.

(16) Level I Adult Cardiovascular Services.

(a) Licensure.

1. A hospital seeking a license for a Level I adult cardiovascular services program shall submit an application on a form provided by the Agency, AHCA Form 3130-8010, August 09, License Application Level I Adult Cardiovascular Services, incorporated herein by reference and available at http://ahca.myflorida.com/MCHQ/Health_Facility_Regulation/Hospital_Outpatient/hospital.shtml#acs, to the Agency, signed by the chief executive officer of the hospital, confirming that for the most recent 12-month period, the hospital has provided a minimum of 300 adult inpatient and outpatient diagnostic cardiac catheterizations or, for the most recent 12-month period, has discharged or transferred at least 300 inpatients with the principal diagnosis of ischemic heart disease (defined by ICD-9-CM codes 410.0 through 414.9).

a. Reportable cardiac catheterization procedures are defined as single sessions with a patient in the hospital’s cardiac catheterization procedure room(s), irrespective of the number of specific procedures performed during the session.

b. Reportable cardiac catheterization procedures shall be limited to those provided and billed for by the Level I licensure applicant and shall not include procedures performed at the hospital by physicians who have entered into block leases or joint venture agreements with the applicant.

2. The request shall confirm the hospital’s intent and ability to comply with the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214; and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention); including guidelines for staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety.

3. The request shall confirm the hospital’s intent and ability to comply with physical plant requirements regarding cardiac catheterization laboratories and operating rooms found in Section 419.2.1.2, Florida Building Code.

4. The request shall also include copies of one or more written transfer agreements with hospitals that operate a Level II adult cardiovascular services program, including written transport protocols to ensure safe and efficient transfer of an emergency patient within 60 minutes. Transfer time is defined as the number of minutes between the recognition of an emergency as noted in the hospital’s internal log and the patient’s arrival at the receiving hospital.

5. All providers of Level I adult cardiovascular services programs shall operate in compliance with subsection 59A-3.2085(13), F.A.C., the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention) guidelines regarding the operation of adult diagnostic cardiac catheterization laboratories and the provision of percutaneous coronary intervention.

6. The applicable guidelines, herein incorporated by reference, are the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214; and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention). Aspects of the guideline related to pediatric services or outpatient cardiac catheterization in freestanding non-hospital settings are not applicable to this rule. Aspects of the guideline related to the provision of elective percutaneous coronary intervention only in hospitals authorized to provide open heart surgery are not applicable to this rule.

7. Hospitals are considered to be in compliance with the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention) guidelines when they adhere to standards regarding staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety. Hospitals must also document an ongoing quality improvement plan to ensure that the cardiac catheterization program and the percutaneous coronary intervention program meet or exceed national quality and outcome benchmarks reported by the American College of Cardiology-National Cardiovascular Data Registry.

8. Level I adult cardiovascular service providers shall report to the American College of Cardiology-National Cardiovascular Data Registry in accordance with the timetables and procedures established by the Registry. All data shall be reported using the specific data elements, definitions and transmission format as set forth by the American College of Cardiology-National Cardiovascular Data Registry.

a. Each hospital licensed to provide Level I adult cardiovascular services shall execute the required agreements with the American College of Cardiology-National Cardiovascular Data Registry to participate in the data registry.

b. Each hospital licensed to provide Level I adult cardiovascular services shall stay current with the payment of all fees necessary to continue participation in the American College of Cardiology-National Cardiovascular Data Registry.

c. Each hospital licensed to provide Level I adult cardiovascular services shall release the data reported by the American College of Cardiology-National Cardiovascular Data Registry to the Agency for Health Care Administration.

d. Each hospital licensed to provide Level I adult cardiovascular services shall use the American College of Cardiology-National Cardiovascular Data Registry data sets and use software approved by the American College of Cardiology for data reporting.

e. Each hospital licensed to provide Level I adult cardiovascular services shall ensure that software formats are established and maintained in a manner that meets American College of Cardiology-National Cardiovascular Data Registry transmission specifications and encryption requirements. If necessary, each hospital shall contract with a vendor approved by the American College of Cardiology-National Cardiovascular Data Registry for software and hardware required for data collection and reporting.

f. To the extent required by the American College of Cardiology-National Cardiovascular Data Registry, each hospital licensed to provide Level I adult cardiovascular services shall implement procedures to transmit data via a secure website or other means necessary to protect patient privacy.

g. Each hospital licensed to provide Level I adult cardiovascular services shall ensure that all appropriate data is submitted on every patient that receives medical care and is eligible for inclusion in the American College of Cardiology-National Cardiovascular Data Registry.

h. Each hospital licensed to provide Level I adult cardiovascular services shall maintain an updated and current institutional profile with the American College of Cardiology-National Cardiovascular Data Registry.

i. Each hospital licensed to provide Level I adult cardiovascular services shall ensure that data collection and reporting will only be performed by trained, competent staff and that such staff shall adhere to the American College of Cardiology-National Cardiovascular Data Registry standards.

j. Each hospital licensed to provide Level I adult cardiovascular services shall submit corrections to any data submitted to the American College of Cardiology-National Cardiovascular Data Registry as discovered by the hospital or by the American College of Cardiology-National Cardiovascular Data Registry. Such corrections shall be submitted within thirty days of discovery of the need for a correction or within such other time frame as set forth by the American College of Cardiology-National Cardiovascular Data Registry. Data submitted must be at a level that the American College of Cardiology-National Cardiovascular Data Registry will include the data in national benchmark reporting.

k. Each hospital licensed to provide Level I adult cardiovascular services shall designate an American College of Cardiology-National Cardiovascular Data Registry site manager that will serve as a primary contact between the hospital, the American College of Cardiology-National Cardiovascular Data Registry and  the Agency with regard to data reporting. The identity of each site manager shall be provided to the Hospital and Outpatient Services Unit at the Agency for Health Care Administration in Tallahassee.

l. By submitting data to the American College of Cardiology-National Cardiovascular Data Registry in the manner set forth herein, each hospital shall be deemed to have certified that the data submitted for each time period is accurate, complete and verifiable.

9. Notwithstanding guidelines to the contrary in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention), all providers of Level I adult cardiovascular services programs may provide emergency and elective percutaneous coronary intervention procedures. Aspects of the guidelines related to pediatric services or outpatient cardiac catheterization in freestanding non-hospital settings are not applicable to this rule.

10. Hospitals with Level I adult cardiovascular services programs are prohibited from providing the following procedures:

a. Any therapeutic procedure requiring transseptal puncture, or

b. Any lead extraction for a pacemaker, biventricular pacer or implanted cardioverter defibrillator.

11. Hospitals with Level I adult cardiovascular services programs must renew their licenses at the time of the hospital licensure renewal, providing the information in two through five above.  Failure to renew the hospital’s license or failure to update the information in two through five above shall cause the license to expire.

(b) Staffing.

1. Each cardiologist shall be an experienced physician who has performed a minimum of 75 interventional cardiology procedures, exclusive of fellowship training and within the previous 12 months from the date of the Level I adult cardiovascular licensure application or renewal application.

2. Physicians with less than 12 months experience shall fulfill applicable training requirements in the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention) prior to being allowed to perform emergency percutaneous coronary interventions in a hospital that is not licensed for a Level II adult cardiovascular services program.

3. The nursing and technical catheterization laboratory staff shall be experienced in handling acutely ill patients requiring intervention or balloon pump. Each member of the nursing and technical catheterization laboratory staff shall have at least 500 hours of previous experience in dedicated cardiac interventional laboratories at a hospital with a Level II adult cardiovascular services program. They shall be skilled in all aspects of interventional cardiology equipment, and must participate in a 24-hour-per-day, 365 day-per-year call schedule.

4. The hospital shall ensure that a member of the cardiac care nursing staff who is adept in hemodynamic monitoring and Intra-aortic Balloon Pump (IABP) management shall be in the hospital at all times.

(c) Emergency Services.

A hospital provider of Level I adult cardiovascular services program must ensure it has systems in place for the emergent transfer of patients with intra-aortic balloon pump support to one or more hospitals licensed to operate a Level II adult cardiovascular services program. Formalized written transfer agreements developed specifically for emergency Percutaneous Coronary Intervention (PCI) patients must be developed with a hospital that operates a Level II adult cardiovascular services program. Written transport protocols must be in place to ensure safe and efficient transfer of a patient within 60 minutes. Transfer time is defined as the number of minutes between the recognition of an emergency as noted in the hospital’s internal log and the patient’s arrival at the receiving hospital. Transfer and transport agreements must be reviewed and tested at least every 3 months, with appropriate documentation maintained.

(d) Policy and Procedure Manual for Medicaid and Charity Care.

1. Each provider of Level I adult cardiovascular services shall maintain a policy and procedure manual, available for review by the Agency, which documents a plan to provide services to Medicaid and charity care patients.

2. At a minimum, the policy and procedure manual shall document specific outreach programs directed at Medicaid and charity care patients for Level I adult cardiovascular services.

(e) Physical Plant Requirements.

Section 419.2.1.2, Florida Building Code, contains the physical plant requirements for adult cardiac catheterization laboratories operated by a licensed hospital.

(f) Enforcement.

1. Enforcement of these rules shall follow procedures established in Rule 59A-3.253, F.A.C.

2. Unless in the view of the Agency there is a threat to the health, safety or welfare of patients, Level I adult cardiovascular services programs that fail to meet provisions of this rule shall be given 15 days to develop a plan of correction that must be accepted by the Agency.

3. Failure of the hospital with a Level I adult cardiovascular services program to make improvements specified in the plan of correction shall result in the revocation of the program license. The hospital may offer evidence of mitigation and such evidence could result in a lesser sanction.

(g) In case of conflict between the provisions of this rule and the guidelines  in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214 and the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention), the provisions of this part shall prevail.

(17) Level II Adult Cardiovascular Services.

(a) Licensure.

1. A hospital seeking a license for a Level II adult cardiovascular services program shall submit an application on a form provided by the Agency, AHCA Form 3130-8011, August 09, License Application Level II Adult Cardiovascular Services, incorporated herein by reference and available at http://ahca.myflorida.com/MCHQ/Health_Facility_Regulation/Hospital_Outpatient /hospital.shtml#acs, to the Agency, signed by the chief executive officer of the hospital, confirming that for the most recent 12-month period, the hospital has provided a minimum of 1,100 adult inpatient and outpatient cardiac catheterizations, of which at least 400 must be therapeutic cardiac catheterizations, or, for the most recent 12-month period, has discharged at least 800 patients with the principal diagnosis of ischemic heart disease (defined by ICD-9-CM codes 410.0 through 414.9).

Reportable cardiac catheterization procedures shall be limited to those provided and billed for by the Level II licensure applicant and shall not include procedures performed at the hospital by physicians who have entered into block leases or joint venture agreements with the applicant.

2. The request shall confirm to the hospital’s intent and ability to comply with applicable guidelines in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards: Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-2; in the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention); and in the ACC/AHA 2004 Guideline Update for Coronary Artery Bypass Graft Surgery: A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (Committee to Update the 1999 Guidelines for Coronary Artery Bypass Graft Surgery) Developed in Collaboration With the American Association for Thoracic Surgery and the Society of Thoracic Surgeons, including guidelines for staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety.

3. The request shall confirm to the hospital’s intent and ability to comply with physical plant requirements regarding cardiac catheterization laboratories and operating rooms found in Section 419.2.1.2, Florida Building Code.

4. All providers of Level II adult cardiovascular services programs shall operate in compliance with subsections 59A-3.2085(13), (16), F.A.C. and the applicable guidelines of the American College of Cardiology/American Heart Association regarding the operation of diagnostic cardiac catheterization laboratories, the provision of percutaneous coronary intervention and the provision of coronary artery bypass graft surgery.

a. The applicable guidelines, herein incorporated by reference, are the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards:  Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214; and

b. ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention; and

c. ACC/AHA 2004 Guideline Update for Coronary Artery Bypass Graft Surgery: A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (Committee to Update the 1999 Guidelines for Coronary Artery Bypass Graft Surgery) Developed in Collaboration With the American Association for Thoracic Surgery and the Society of Thoracic Surgeons.

d. Aspects of the guidelines related to pediatric services or outpatient cardiac catheterization in freestanding non-hospital settings are not applicable to this rule.

5. Hospitals are considered to be in compliance with the guidelines in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards:  Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214; in the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention; and in the ACC/AHA 2004 Guideline Update for Coronary Artery Bypass Graft Surgery: A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (Committee to Update the 1999 Guidelines for Coronary Artery Bypass Graft Surgery) Developed in Collaboration With the American Association for Thoracic Surgery and the Society of Thoracic Surgeons when they adhere to standards regarding staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety. Hospitals must also document an ongoing quality improvement plan to ensure that the cardiac catheterization program, the percutaneous coronary intervention program and the cardiac surgical program meet or exceed national quality and outcome benchmarks reported by the American College of Cardiology-National Cardiovascular Data Registry and the Society of Thoracic Surgeons.

6. In addition to the requirements set forth in subparagraph (16)(a)7. of this rule, each hospital licensed to provide Level II adult cardiovascular services programs shall participate in the Society of Thoracic Surgeons National Database.

a. Each hospital licensed to provide Level II adult cardiovascular services shall report to the Society of Thoracic Surgeons National Database in accordance with the timetables and procedures established by the Database. All data shall be reported using the specific data elements, definitions and transmission format as set forth by the Society of Thoracic Surgeons.

b. Each hospital licensed to provide Level II adult cardiovascular services shall stay current with the payment of all fees necessary to continue participation in the Society of Thoracic Surgeons National Database.

c. Each hospital licensed to provide Level II adult cardiovascular services shall release the data reported by the Society of Thoracic Surgeons National Database to the Agency.

d. Each hospital licensed to provide Level II adult cardiovascular services shall use the most current version of the Society of Thoracic Surgeons National Database and use software approved by the Society of Thoracic Surgeons for data reporting.

e. Each hospital licensed to provide Level II adult cardiovascular services shall ensure that software formats are established and maintained in a manner that meets Society of Thoracic Surgeons transmission specifications and encryption requirements.  If necessary, each hospital shall contract with a vendor approved by the Society of Thoracic Surgeons National Database for software and hardware required for data collection and reporting.

f. To the extent required by the Society of Thoracic Surgeons National Database, each hospital licensed to provide Level II adult cardiovascular services shall implement procedures to transmit data via a secure website or other means necessary to protect patient privacy.

g. Each hospital licensed to provide Level II adult cardiovascular services shall ensure that all appropriate data is submitted on every patient who receives medical care and is eligible for inclusion in the Society of Thoracic Surgeons National Database.

h. Each hospital licensed to provide Level II adult cardiovascular services shall maintain an updated and current institutional profile with the Society of Thoracic Surgeons National Database.

i. Each hospital licensed to provide Level II adult cardiovascular services shall ensure that data collection and reporting will only be performed by trained, competent staff and that such staff shall adhere to Society of Thoracic Surgeons National Database standards.

j. Each hospital licensed to provide Level II adult cardiovascular services shall submit corrections to any data submitted to the Society of Thoracic Surgeons National Database as discovered by the hospital or by the Society of Thoracic Surgeons National Database.  Such corrections shall be submitted within thirty days of discovery of the need for a correction or within such other time frame as set forth by the Society of Thoracic Surgeons National Database. Data submitted must be at a level that the Society of Thoracic Surgeons National Database will include the data in national benchmark reporting.

k. Each hospital licensed to provide Level II adult cardiovascular services shall designate a Society of Thoracic Surgeons National Database site manager that will serve as a primary contact between the hospital, the  Society of Thoracic Surgeons National Database and the Agency with regard to data reporting. The identity of each site manager shall be provided to the Hospital and Outpatient Services Unit at the Agency for Health Care Administration in Tallahassee.

l. By submitting data to the Society of Thoracic Surgeons National Database and the American College of Cardiology-National Cardiovascular Data Registry in the manner set forth herein, each hospital shall be deemed to have certified that the data submitted for each time period is accurate, complete and verifiable.

7. Hospitals with Level II adult cardiovascular services programs must renew their licenses at the time of the hospital licensure renewal, providing the information in two through four above. Failure to renew the hospital’s license or failure to update the information in two through four above shall cause the license to expire.

(b) Staffing.

1. Each cardiac surgeon shall be Board certified.

a. New surgeons shall be Board certified within 4 years after completion of their fellowship.

b. Experienced surgeons with greater than 10 years experience shall document that their training and experience preceded the availability of Board certification.

2. Each cardiologist shall be an experienced physician who has performed a minimum of 75 interventional cardiology procedures, exclusive of fellowship training and within the previous 12 months from the date of the Level II adult cardiovascular licensure application or renewal application.

3. The nursing and technical catheterization laboratory staff shall be experienced in handling acutely ill patients requiring intervention or balloon pump. Each member of the nursing and technical catheterization laboratory staff shall have at least 500 hours of previous experience in dedicated cardiac interventional laboratories at a hospital with a Level II adult cardiovascular services program. They shall be skilled in all aspects of interventional cardiology equipment, and must participate in a 24-hour-per-day, 365 day-per-year call schedule.

4. The hospital shall ensure that a member of the cardiac care nursing staff who is adept in hemodynamic monitoring and Intra-aortic Balloon Pump (IABP) management shall be in the hospital at all times.

(c) Policy and Procedure Manual for Medicaid and Charity Care.

1. Each provider of adult Level II adult cardiovascular services shall maintain a policy and procedure manual, available for review by the Agency, which documents a plan to provide services to Medicaid and charity care patients.

2. At a minimum, the policy and procedure manual shall document specific outreach programs directed at Medicaid and charity care patients for Level II adult cardiovascular services.

(d) Physical Plant Requirements.

Section 419.2.1.2, Florida Building Code, contains the physical plant requirements for adult cardiac catheterization laboratories and operating rooms for cardiac surgery operated by a licensed hospital.

(e) Enforcement.

1. Enforcement of these rules shall follow procedures established in Rule 59A-3.253, F.A.C.

2. Unless in the view of the Agency there is a threat to the health, safety or welfare of patients, Level II adult cardiovascular services programs that fail to meet provisions of this rule shall be given 15 days to develop a plan of correction that must be accepted by the Agency.

3. Failure of the hospital with a Level II adult cardiovascular services program to make improvements specified in the plan of correction shall result in the revocation of the program license. The hospital may offer evidence of mitigation and such evidence could result in a lesser sanction.

(f) In case of conflict between the provisions of this rule and the guidelines in the American College of Cardiology/Society for Cardiac Angiography and Interventions Clinical Expert Consensus Document on Cardiac Catheterization Laboratory Standards:  Bashore et al, ACC/SCA&I Clinical Expert Consensus Document on Catheterization Laboratory Standards, JACC Vol. 37, No. 8, June 2001: 2170-214; the ACC/AHA/SCAI 2005 Guideline Update for Percutaneous Coronary Intervention A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (ACC/AHA/SCAI Writing Committee to Update the 2001 Guidelines for Percutaneous Coronary Intervention; and the ACC/AHA 2004 Guideline Update for Coronary Artery Bypass Graft Surgery: A Report of the American College of Cardiology/American Heart Association Task Force on Practice Guidelines (Committee to Update the 1999 Guidelines for Coronary Artery Bypass Graft Surgery) Developed in Collaboration With the American Association for Thoracic Surgery and the Society of Thoracic Surgeons, the provisions of this part shall prevail.

(18) Burn Units.

(a) All licensed hospitals that operate burn units under Section 408.0361(2), F.S., shall comply with the guidelines published by the American College of Surgeons, Committee on Trauma. Hospitals are considered to be in compliance with the American College of Surgeons guidelines when they adhere to guidelines regarding staffing, physician training and experience, operating procedures, equipment, physical plant, and patient selection criteria to ensure patient quality and safety. The applicable guidelines, herein incorporated by reference, are “Guidelines for the Operation of Burn Centers,” in Resources for Optimal Care of the Injured Patient, Committee on Trauma, American College of Surgeons, (2006); Chapter 14, pages 79 through 86. These guidelines are available at: http://www.ameriburn.org/Chapter14.pdf . The determination of compliance with the guidelines is based on the burn unit providing evidence of verification from the American Burn Association.

(b) A hospital may apply for the initial licensure of a burn unit by submitting a hospital licensure application as specified in paragraph 59A-35.060(1)(h), F.A.C., indicating the addition of burn unit services, and attaching License Application Burn Unit Services, AHCA Form 3130-8012, August, 2010, incorporated herein by reference. Both of these forms are available at: http://ahca.myflorida.com/MCHQ/Health_Facility_Regulation/Hospital_Outpatient/hospital.shtml. The applicant should complete this form indicating the date that burn unit services will begin and that the hospital is in partial compliance with “Guidelines for the Operation of Burn Centers” but has not received initial verification as a burn unit. A burn unit is considered to be in partial compliance with the guidelines until it demonstrates that it admits an annual average of 100 or more patients with acute burn injuries, averaged over a three-year period, and meets all other guidelines. During this initial licensure period, the hospital license will indicate that the burn unit is “provisional”. Upon completion of the verification process with the American Burn Association, the provisional status will be lifted, the burn unit will be fully licensed with the service listed on the hospital license. The license application form must be signed by the hospital’s Chief Executive Officer.

(c) Burn units that were in operation prior to June 30, 2004 shall be considered grandfathered and authorized to operate as a burn unit with service listed on their hospital license. The grandfathered licensure shall be effective for three years from the adoption of this rule but burn units that were in operation prior to June 30, 2004 shall be required to meet the promulgated licensure rules and receive verification from the American Burn Association within three years of the effective date of this rule.

(d) At the time of licensure renewal, burn unit operators shall submit current documentation from the American Burn Association that verifies the hospital’s adherence to the guidelines incorporated in paragraph (18)(b).

(e) Each provider of burn unit services shall maintain a policy and procedure manual, available for review by the Agency, which documents a plan to provide services to Medicaid and charity care patients.

(f) Enforcement of these rules shall follow procedures established in Rule 59A-3.253, F.A.C.

Rulemaking Authority 395.1055, 395.3038, 395.401, 408.036, 408.036(1), 408.0361(2) FS. Law Implemented 395.001, 395.1055, 395.1065, 395.3038, 395.401, 408.036, 408.0361, 957.05 FS. History–New 4-17-97, Amended 3-29-98, 8-23-99, 3-23-06, 1-8-09, 11-3-09, 1-11-11.

## 59A-3.250 Surveillance, Prevention, and Control of Infection.

(1) Each hospital shall establish an infection control program involving members of the organized medical staff, the nursing staff, other professional staff as appropriate, and administration. The program shall provide for:

(a) The surveillance, prevention, and control of infections among patients and personnel;

(b) The establishment of a system for identifying, reporting, evaluating and maintaining records of infections;

(c) Ongoing review and evaluation of all septic, isolation and sanitation techniques employed in the hospital; and

(d) Development and coordination of training programs in infection control for all hospital personnel.

(2) Each hospital shall have written policies and procedures reflecting the scope of the infection control program outlined in subsection (1). The written policies and procedures shall be reviewed at least every two years by the infection control program members, dated at the time of each review, revised as necessary, and enforced.

(3) The policies and procedures devised by the infection control program shall be approved by the governing body, and shall contain at least the following:

(a) Specific policies for the shelf life of all stored sterile items.

(b) Specific policies and procedures related to occupational exposure to blood and body fluids.

(c) Specific policies and procedures related to admixture and drug reconstitution, and to the manufacture of intravenous and irrigating fluids.

(d) Specific policies related to the handling and disposal of biomedical waste in accordance with Chapter 64E-16, F.A.C., May 1995, OSHA 29 CFR Part 1910.1030 Occupational Exposure to Blood Borne Pathogens Final Rule, July 1995, and the Department of Environmental Protection Code Chapter 62-712 on Biomedical Waste, May 1995.

(e) Specific policies related to the selection, storage, handling, use and disposition of disposable items.

(f) Specific policies related to decontamination and sterilization activities performed in central services and throughout the hospital, including a requirement that steam gas (ETO) and hot air sterilizers be tested with live bacterial spores at least weekly.

(g) Specific policies regarding the indications for universal precautions, body substance isolation, CDC isolation guidelines, or equivalent and the types of isolation to be used for the prevention of the transmission of infectious diseases.

(h) A requirement that soiled linen is collected in such a manner as to minimize microbial dissemination into the environment.

(i) A requirement that all cases of communicable diseases as set forth in Chapter 64D-3, F.A.C., be promptly and properly reported in accordance with the provisions of that rule.

(4) The individuals involved in the infection control program shall meet at least quarterly, shall maintain written minutes of all meetings, and shall make a report at least annually to the assigned professional staff and the governing body.

(5) Each hospital shall establish an employee health policy to minimize the likelihood of transmission of communicable disease by both employees and patients. Such policies shall include work restrictions for an employee whenever it is likely that communicable disease may be transmitted until such time as a medical practitioner certifies that the employee may return to work.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1011, 395.1055 FS. History–New 9-4-95, Formerly 59A-3.215.

## 59A-3.251 Hospital Reporting of Exposure to Selected Infectious Diseases.

The licensed facility shall establish a written policy and procedure for notifying EMTs, paramedics or their emergency medical transportation service employer, or other persons known to have been exposed to a patient with a selected infectious disease while transporting or treating an ill or injured patient to that licensed facility. Selected infectious diseases are defined as Acquired Immunodeficiency Syndrome; anthrax; syphilis in an infectious stage; diphtheria; disseminated vaccinia; Hansen’s disease; hepatitis A; hepatitis B; hepatitis non A, non B, Legionnaire’s disease; malaria; measles; meningococcal meningitis; plague; poliomyelitis, psittacosis; pulmonary tuberculosis; Q fever; rabies; rubella; typhoid fever. Each licensed facility shall designate a person or persons to notify the EMT’s, paramedics or their emergency medical transportation service employer or other persons known to have been exposed to a patient with a selected infectious disease. These procedures shall include at a minimum the following:

(1) Notification of exposure to a selected infectious disease, either verbal or written, must take place within 48 hours of a confirmed diagnosis.

(2) Verbal notification of such exposure to a selected infectious disease must be followed by written notification within 48 hours of a confirmed diagnosis.

(3) Identification of EMT, paramedic, or other known persons to have been in contact with the patient during treatment or transport, if notification is made to the EMS provider.

(4) Both written and verbal notification shall contain at a minimum:

(a) Name of disease;

(b) Signs and symptoms of clinical disease;

(c) Date of exposure to the selected infectious disease;

(d) Incubation period of disease;

(e) Mode of spread of the disease;

(f) Advisement of appropriate diagnosis, prophylaxis, and treatment, if any.

(5) Confidentiality of patient information must be maintained. The name of the patient shall not be disclosed.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1025 FS. History–New 3-11-86, Formerly 10D-28.131, Amended 4-17-97, Formerly 59A-3.131.

## 59A-3.252 Classification of Hospitals.

(1) The agency will license four classes of facilities:

(a) Class I or general hospitals which includes;

1. General acute care hospitals with an average length of stay of 25 days or less for all beds;

2. Long term care hospitals, which meet the provisions of subsection 59A-3.065(34), F.A.C.; and

3. Rural hospitals designated under Section 395, Part III, F.S.

(b) Class II specialty hospitals offering the range of medical services offered by general hospitals, but restricted to a defined age or gender group of the population which includes;

1. Specialty hospitals for children; and

2. Specialty hospitals for women.

(c) Class III specialty hospitals offering a restricted range of services appropriate to the diagnosis, care, and treatment of patients with specific categories of medical or psychiatric illnesses or disorders which include;

1. Specialty medical hospitals;

2. Specialty rehabilitation hospitals;

3. Specialty psychiatric hospitals, which may include beds licensed to offer Intensive Residential Treatment programs;

4. Specialty substance abuse hospitals, which may include beds licensed to offer Intensive Residential Treatment programs; and

(d) Class IV specialty hospitals restricted to offering Intensive Residential Treatment Programs for Children and Adolescents, pursuant to Section 395.002(16), F.S.

(2) In addition to other requirements specified in these rules, all licensed hospitals shall have at least the following:

(a) Inpatient beds;

(b) A governing authority legally responsible for the conduct of the hospital;

(c) A chief executive officer or others similarly titled official to who the governing authority delegates the full-time authority for the operation of the hospital in accordance with the established policy of the governing authority;

(d) An organized medical staff to which the governing authority delegates responsibility for maintaining proper standards for medical and other health care;

(e) A current and complete medical record for each patient admitted to the hospital;

(f) A policy requiring that all patients be admitted on the authority of and under the care of a member of the organized medical staff;

(g) Facilities and professional staff available to provide food to patients to meet their nutritional needs;

(h) A procedure for providing care in emergency cases;

(i) A method and policy for infection control; and

(j) An on-going organized program to enhance the quality of patient care and review the appropriateness of utilization of services.

(3) In addition to the requirements of subsection (2) and other requirements of these rules, Class I, and Class II hospitals shall have at least the following:

(a) One licensed registered nurse on duty at all times on each floor or similarly titled part of the hospital for rendering patient care services;

(b) A pharmacy supervised by a licensed pharmacist either in the facility or by contract sufficient to meet patient needs;

(c) Diagnostic imaging services either in the facility or by contract sufficient to meet patient needs;

(d) Clinical laboratory services either in the facility or by contract sufficient to meet patient needs;

(e) Operating room services; and

(f) Anesthesia service.

(4) In addition to the requirements of subsection (2) and other requirements of these rules, all Class II, Class III, and Class IV hospitals shall provide the treatment services, equipment, supplies and staff appropriate to the particular category of patients treated at the facility.

(5) All Class III hospitals, in addition to meeting the requirements of subsection (2) and other requirements of these rules, must provide:

(a) For at least one qualified staff person at all times on each floor or similarly titled part of the hospital for rendering patient care services;

(b) A pharmacy supervised by a licensed pharmacist either in the facility or by contract sufficient to meet patient needs;

(c) Diagnostic imaging services either in the facility or by contract sufficient to meet patient needs;

(d) Clinical laboratory services, either in the facility or by contract sufficient to meet patient needs; and

(e) Any other services, when provided by a Class III or Class IV hospital, shall meet the standards pertinent to that particular service as promulgated in Rules 59A-3.065 through 59A-3.312, F.A.C., as applicable.

Rulemaking Authority 395.1055 FS. Law Implemented 395.002, 395.1055, 408.035, 408.036 FS. History–New 9-4-95, Formerly 59A-3.202.

## 59A-3.253 Investigations and License, Life Safety and Validation Inspections.

(1) INSPECTIONS. – The AHCA shall conduct periodic inspections of hospitals in order to ensure compliance with all licensure requirements, and as it deems necessary to carry out the functions of the agency. Inspections shall be conducted for the following reasons:

(a) To assure compliance with the licensure and life safety requirements of this Chapter;

(b) To validate the inspection process of hospital accrediting organizations;

(c) To respond to licensure, life safety, and emergency access complaints; or

(d) To protect the public health and safety.

(2) NON-ACCREDITED HOSPITALS. – Hospitals which are not accredited by a hospital accrediting organization will be subject to a scheduled annual licensure inspection survey.

(a) Within 10 calendar days of the completion of the agency’s survey, the agency will mail a copy of the survey findings to the hospital. For those hospitals determined not in compliance with state licensure requirements, the notification shall include a statement of deficiencies.

(b) Within 10 calendar days of the receipt of the statement of deficiencies, the hospital must prepare and mail a plan of correction for review and approval by the agency. The plan of correction must address the action planned by the hospital to correct each deficiency, the individuals or entities responsible for implementing the corrective action, and the date by which each corrective action will be completed.

(c) The agency will, if necessary, conduct a follow-up visit to a hospital with an acceptable plan of correction within 30 days of the completion date for all deficiencies contained in the plan of correction, or will review pertinent materials submitted by the hospital, to determine compliance with the approved plan of correction.

(d) The agency will work with hospitals to ensure compliance with standards of care through the implementation of acceptable plans of correction. Those hospitals which fail to implement an approved plan of correction will be subject to sanctions imposed under Section 395.1065, F.S.

(3) ACCREDITED HOSPITALS. – The agency shall accept the survey report of an accrediting organization in lieu of an annual licensure inspection for accredited hospitals and for hospitals seeking accreditation by a hospital accrediting organization, provided that the standards included in the survey report of the accrediting organization are determined by the agency to document that the hospital is in substantial compliance with state licensure requirements, and the hospital does not meet the criteria specified under subparagraphs (e)1. and 2.

(a) Upon receipt of the accrediting organization’s survey report, the agency will review the findings to determine if the hospital is in substantial compliance with state licensure requirements.

(b) The agency shall notify the hospital within 60 days of the receipt of the accrediting organization’s survey report regarding the agency’s determination of the hospital's compliance or non-compliance with state licensure requirements. For hospitals that are determined not in compliance with licensure requirements, the notification will include a statement of deficiencies.

(c) Hospitals determined by the agency to be not in substantial compliance with licensure requirements, based on the accreditation report, shall submit a plan of correction to the agency within 10 calendar days of receipt of the statement of deficiencies.

(d) The agency shall review the plan of correction in accordance with the procedures specified under paragraphs (2)(a) through (d).

(e) Hospitals that are determined by the agency to be in substantial compliance with licensure requirements will not be subject to an annual licensure inspection except under the following circumstances:

1. The hospital has been denied accreditation or has received a provisional or conditional accreditation from a hospital accrediting organization on its most recent accreditation survey, and has not submitted an acceptable plan of correction to the accrediting organization and the agency;

2. The hospital has received full accreditation but has not authorized the release of the report to the agency, or has not ensured that the agency received the accrediting organization’s survey report prior to the agency scheduling a licensure inspection.

(4) LICENSURE INSPECTION FEES. – With the exception of state-operated licensed facilities, the licensure inspection fee shall be $12.00 per hospital bed, provided that no licensed facility shall be assessed less than $400.00 per inspection for licensure, and further provided that a separate fee for the licensure inspection shall be charged for each hospital located on a separate premises, regardless of its inclusion on a single license.

(5) LIFE SAFETY INSPECTIONS. – The AHCA shall conduct a scheduled annual life safety inspection of all licensed hospitals to ensure physical plant compliance with life safety codes and requirements for disaster preparedness, pursuant to this Chapter, unless:

(a) The hospital was surveyed during an accreditation survey by a Florida accredited life safety inspector, and found to be in compliance with life safety requirements by the accrediting organization, and;

(b) The report of that survey has been released to and received by the AHCA prior to the agency scheduling a life safety inspection.

(6) LIFE SAFETY INSPECTION FEES. – With the exception of state-operated licensed facilities, the fee for a life safety inspection shall be $1.50 per hospital bed, provided that no licensed facility shall be assessed less than $40 for a life safety inspection, and further provided that a separate fee for the life safety inspection shall be charged for each hospital located on a separate premises, regardless of its inclusion on a single license. A separate fee for a life safety inspection will not be assessed when conducted as part of a licensure or validation inspection.

(7) VALIDATION INSPECTIONS. – Each year, the agency shall conduct validation inspections on a minimum of five percent of those hospitals that have undergone a full accreditation inspection from a hospital accrediting organization, within 60 days of the accreditation survey, to determine ongoing compliance with licensure requirements.

(a) Within 10 calendar days following the completion of a licensure validation survey, the agency will mail a copy of its findings to the hospital. For those hospitals determined not in compliance with licensure requirements, the notification will include a statement of deficiencies.

(b) Facilities found not in compliance based on a validation inspection shall submit a plan of correction as specified under paragraphs (2)(a) through (d).

(c) If the agency determines, based on the results of validation survey findings, that a fully accredited hospital is not in substantial compliance with licensure requirements, the agency shall report its findings to the accrediting organization and shall conduct a full licensure inspection on that hospital during the following year.

(d) The fee for conducting a licensure validation inspection shall be the same as that specified for licensure inspections under subsection (4). A separate fee for a validation survey will not be assessed when conducted in conjunction with a Medicare certification survey.

(8) COMPLAINT INSPECTIONS. – The agency shall conduct investigations of complaints regarding violations of licensure and life safety in accordance with Section 395.0161, F.S., and emergency access requirements in accordance with Section 395.1046, F.S. Complaint investigations will be unannounced. An entrance conference must be conducted upon arrival, by agency personnel investigating the complaint, to inform the hospital’s administrator about the nature of the complaint investigation and to answer questions from hospital staff. An exit conference must be provided at the conclusion of the on-site investigation to inform the hospital of the scope of the investigation and to receive any additional information that the hospital wishes to furnish.

(a) Upon receipt of a complaint, the agency shall review the complaint for compliance with licensure issues, and in addition, shall take the following action:

1. Complaints involving accredited hospitals shall be reported to the appropriate accrediting organization;

2. Complaints involving Medicare certified hospitals shall be referred to the Health Care Finance Administration for a determination as to the need for an investigation under certification standards.

3. Complaints involving diagnostic radiology equipment or personnel, sanitation, waste disposal, or food preparation shall be referred to the Department of Health and Rehabilitative Services for investigation.

(b) Upon a determination that further investigation of a complaint is warranted, the agency shall conduct an investigation within 90 days, unless there is an immediate threat, in which case an immediate inspection will be undertaken.

(c) Upon conclusion of a complaint investigation by the agency, the agency shall notify the affected parties in writing within 10 calendar days of its determination as to the validity of the complaint and any actions to be taken to resolve violations or sanctions imposed against the hospital.

(d) Hospital personnel and physicians shall report any apparent violations of emergency access requirements under Section 395.1041, F.S., to the agency, and shall include all relevant information. Reports shall be made within 30 days following the occurrence. Medical personnel reasonably believed by the agency to be in violation of these rules will immediately be referred by the agency to their respective licensing boards. Violations include failure to report when on-call or intentionally misrepresenting the patient’s condition in cases of medically necessary transfers or in determining the presence or absence of an emergency medical condition or rendering appropriate emergency services and care, or failure or refusal to sign a certificate of transfer as required by this section.

(9) CONFORMANCE WITH ACCREDITATION STANDARDS. – In all hospitals where the agency does not conduct, by reason of the hospital’s accreditation status, either an annual licensure inspection or an annual life safety inspection, the hospital shall continue to conform to the standards of accreditation throughout the term of accreditation, or shall notify the agency of the areas of non-conformance. Where the agency is notified of non-conformance, it shall take appropriate action as specified under subsection 59A-3.253(6), F.A.C.

(10) DATA COLLECTION. – All hospitals shall comply with the agency requirements for data submission as authorized under Section 395.1055, F.S., Chapters 408 and 732, F.S. This data, which does not have to be resubmitted to the agency’s hospital licensing office as a provision of this part, includes:

(a) Certificate of need reviews required under Sections 408.031 through 408.045, F.S., and at such intervals as required by Chapter 59C-1, F.A.C.;

(b) Quality of care patient outcome data as required by Sections 408.061(1) and 395.1055(1)(g), F.S., and as mandated by rules adopted by the agency;

(c) Completion of the Specialty Care and Referrals Report, as required by rules adopted by the agency; and

(d) Each hospital shall submit a quarterly report to the agency summarizing the number of requests made by the hospital for organ donation in accordance with Chapter 732, F.S.

(e) All hospitals shall make available on their Internet websites a description of and link to the Agency for Health Care Administration webpage which contains the hospital patient charge and performance outcome data that is collected pursuant to Section 408.061(1), F.S. and, if requested, hospitals shall provide a hard copy of the description and the link.

(11) SANCTIONS. – The agency shall impose sanctions, in accordance with Section 395.1065, F.S., on those hospitals which fail to submit an acceptable plan of correction or implement actions to correct deficiencies identified by the agency or an appropriate accrediting organization which are specified in an approved plan of correction or as identified as a result of a complaint investigation.

Rulemaking Authority 395.0161, 395.1055 FS. Law Implemented 395.003, 395.0161, 395.1055, 408.035, 408.036 FS. History–New 9-4-95, Formerly 59A-3.204 Amended 5-16-06.

## 59A-3.254 Patient Rights and Care.

(1) Patient Assessment. Each hospital shall develop and adopt policies and procedures to ensure an initial assessment of the patient’s physical, psychological and social status, appropriate to the patient’s developmental age, is completed to determine the need and type of care or treatment required, and the need for further assessment. The scope and intensity of the initial assessment shall be determined by the patient’s diagnosis, the treatment setting, the patient’s desire for treatment, and response to previous treatment.

(a) Such policies shall:

1. Specify the time period preceding or following admission within which the initial assessment shall be conducted;

2. Require that the initial assessment be documented in writing in the patient’s medical record;

(b) The initial assessment shall determine the need for an assessment of the patient’s nutritional and functional status, as well as discharge planning needs, when appropriate;

(c) The hospital shall have policies and procedures to ensure that periodic reassessments of the patient are conducted based on changes in either the patient’s condition, diagnosis, or response to treatment;

(d) The hospital shall ensure that care and treatment decisions are based on the patient’s identified needs and treatment priorities;

(e) An individualized treatment plan shall be developed for each patient based upon the initial assessment and other diagnostic information as appropriate.

(2) Coordination of Care. Each hospital shall develop and implement policies and procedures on discharge planning which address:

(a) Identification of patients requiring discharge planning;

(b) Initiation of discharge planning on a timely basis;

(c) The role of the physician, other health care givers, the patient, and the patient’s family in the discharge planning process; and

(d) Documentation of the discharge plan in the patient’s medical record including an assessment of the availability of appropriate services to meet identified needs following hospitalization.

(3) Patient and Family Education.

(a) General Provisions. Each hospital shall develop a systematic approach to educating the patient and family to improve patient outcomes by promoting recovery, speedy return to function, promoting healthy behaviors, and involving patients in their care and care decisions.

(b) Each hospital shall provide the patient and family with education specific to the patient’s assessed needs, capabilities, and readiness. Such education shall include when indicated:

1. An assessment when indicated, of the educational needs, capabilities, and readiness to learn based on cultural and religious practices, emotional barriers, desire and motivation to learn, physical and cognitive limitations, and language barriers;

2. Instruction in the specific knowledge or skills needed by the patient or family to meet the patient’s ongoing health care needs including:

a. The use of medications.

b. The use of medical equipment.

c. Potential drug or food interactions, and nutritional intervention or modified diets.

d. Rehabilitation techniques.

e. Available community resources.

f. When and how to obtain further treatment; and

g. The patient’s and family’s responsibilities in the treatment process.

3. Information about any discharge instructions given to the patient or family shall be provided to the organization or individual responsible for providing continuing care.

4. Each hospital shall plan and support the provision and coordination of patient and family education activities by ensuring that:

a. Educational resources required are identified and made available; and

b. The educational process is interdisciplinary, as appropriate to the plan of care.

(4) Patient Rights. Each hospital shall develop and adopt policies and procedures to ensure the following rights of the patient:

(a) The right to refuse treatment and life-prolonging procedures as specified under Section 765.1105, F.S.;

(b) The right to formulate advance directives and designate a surrogate to make health care decisions on behalf of the patient as specified under Chapter 765, F.S. The policies shall not condition treatment or admission upon whether or not the individual has executed or waived an advance directive. In the event of conflict between the facility’s policies and procedures and the individual’s advance directive, provision should be made in accordance with Section 765.308, F.S. Policies shall include:

1. Provide each adult individual, at the time of the admission as an inpatient, with a copy of “Health Care Advance Directives – The Patient’s Right to Decide,” effective 1-11-93, which is hereby incorporated by reference, or with a copy of some other substantially similar document which is a written description of Chapter 765, F.S., regarding advance directives;

2. Providing each adult individual, at the time of admission as an inpatient, with written information concerning the health care facility’s policies respecting advance directives; and

3. The requirement that documentation of the existence of an advance directive be contained in the medical record. A health care facility which is provided with the individual’s advance directive shall make the advance directive or a copy thereof a part of the individual’s medical record.

(c) The right to information about patient rights as set forth in Section 381.026, F.S., and procedures for initiating, reviewing and resolving patient complaints;

(d) The right to participate in the consideration of ethical issues that arise in the care of the patient;

(e) The right to personal privacy and confidentiality of information including access to information contained in the patient’s medical records as specified under Section 395.3025, F.S.;

(f) The right of the patient’s next of kin or designated representative to exercise rights on behalf of the patient;

(g) The right to an itemized patient bill upon request as specified under Section 395.301, F.S.;

(h) The right to be free of restraints consistent with the rights of mentally ill persons or patients as provided in Section 394.459, F.S.

(5) In addition to the provisions of this section, hospitals must comply with Section 381.026, F.S., which remains in effect.

Rulemaking Authority 395.003, 395.1055 FS. Law Implemented 395.003, 395.1055 FS. History–New 4-17-97, Formerly 59A-3.2055.

## 59A-3.255 Emergency Care.

(1) SIGNAGE REQUIREMENTS.

(a) Each hospital offering emergency services and care shall post, in a conspicuous place in the emergency service area, a sign clearly stating a patient’s right to emergency services and care as set forth in Section 395.1041, F.S. The sign shall be posted in both English and in Spanish.

(b) Each hospital offering emergency services and care shall post a sign identifying the service capability of the hospital. The categories of services listed on the sign may be general in nature if the sign refers patients to another location within that facility where a list of the subspecialties is available. The sign identifying the service capability of the hospital and the additional listing of subspecialties, if a separate subspecialty list is maintained, shall be in both English and in Spanish.

(c) The signs required by this rule section shall be posted in a location where individuals not yet admitted to the hospital would reasonably be expected to present themselves for emergency services and care.

(2) TRANSFER PROCEDURES. Each hospital providing emergency services and care shall establish policies and procedures which incorporate the requirements of Chapter 395, F.S., relating to emergency services. The policies and procedures shall incorporate at a minimum:

(a) Decision protocols identifying the emergency services personnel within the hospital responsible for the arrangement of outgoing and incoming transfers;

(b) Decision protocols stating the conditions that must be met prior to the transfer of a patient to another hospital. These conditions are:

1. If a patient, or a person who is legally responsible for the patient and acting on the patient’s behalf, after being informed of the hospital’s obligation under Chapter 395, F.S., and of the risk of transfer, requests that the transfer be effected; or

2. If a physician has signed a certification that, based upon the reasonable risks and benefits to the patient, and based upon the information available at the time of transfer, the medical benefits reasonably expected from the provision of appropriate medical treatment at another hospital outweigh the increased risks to the individual’s medical condition from effecting the transfer; or

3. If a physician is not physically present in the emergency services area at the time an individual is transferred, a qualified medical person may sign a certification that a physician with staff privileges at the transferring hospital, in consultation with such personnel, has determined that the medical benefits reasonably expected from the provision of appropriate medical treatment at another medical facility outweigh the increased risks to the individual’s medical condition from effecting the transfer. The certification shall summarize the basis for such determination. The consulting physician must sign the certification within 72 hours of the transfer.

(c) A provision providing that all medically necessary transfers shall be made to the geographically closest hospital with the service capability, unless another prior arrangement is in place or the geographically closest hospital is at service capacity as stated in Section 395.1041(3)(e), F.S.

(d) Protocols for maintaining records of patient transfers made or received for a period of five years. Patient transfer information shall be incorporated separately in transfer logs and into the patient’s permanent medical record as stated in Section 395.1041(4)(a)1, F.S.

(e) Documentation of all current transfer arrangements that have been made with other hospitals and physicians.

(f) A copy of Section 395.1041, F.S., Access to Emergency Services and Care, and a copy of these rules.

(g) Provisions for informing hospital emergency services personnel and medical staff of the hospital’s emergency service policies and procedures, having at a minimum, the requirement to provide emergency services and care pursuant to Section 395.1041, F.S.

(3) INVENTORY REPORTING.

(a) Pursuant to Section 395.1041, F.S., the agency is responsible for compiling an inventory of hospitals with emergency services. This inventory shall list all services within the service capability of the hospital. A copy of this inventory may be obtained by contacting the Agency for Health Care Administration, Division of Health Quality Assurance, Ft. Knox Office Building, 2727 Mahan Drive, Tallahassee, Florida, 32308. The per page duplication costs will be computed in accordance with Chapter 119, F.S.

(b) Every hospital offering emergency services and care shall report to the agency for inclusion in the inventory those services which are within the service capability of the hospital. The following services, when performed on an infrequent and short time limited basis, are not considered to be within the service capability of the hospital:

1. Services performed for investigative purposes under the auspices of a federally approved institutional review board; or

2. Services performed for educational purposes; or

3. Emergencies performed by physicians who are not on the active medical staff of the reporting hospital.

(c) Any addition of service shall be reported to the agency prior to the initiation of the service. The agency will act accordingly to include the service in the next publication of the inventory and to add the service on the face of the hospital license.

(d) If the agency has reason to believe that a hospital offers a service and the service was not reported on the inventory, the agency will notify the hospital and provide the hospital with an opportunity to respond. The agency shall arrange for an on-site visit prior to the agency’s determination of capability, with advance notice of the on-site visit. If, after investigation, the agency determines that a service is offered by the hospital as evidenced by the patient medical records or itemized bills, the agency shall amend the inventory and the face of the hospital license.

(4) EXEMPTIONS.

(a) Every hospital providing emergency services shall ensure the provision of services within the service capability of the hospital, 24 hours per day, 7 days per week either directly or indirectly through:

1. An agreement with another hospital made prior to receipt of a patient in need of the service; or

2. An agreement with one or more physicians made prior to receipt of a patient in need of the service; or

3. Any other arrangement made prior to receipt of a patient in need of the service.

(b) If a hospital has determined that it is unable to provide a service on a 24 hour per day, 7 day per week basis, either directly or indirectly through arrangement with another hospital or physician(s), the hospital must file an application with the agency to request a service exemption. The application must identify the service for which the hospital is requesting an exemption. This information shall be submitted to the agency on AHCA Form 3000-1, effective July 1993 which is incorporated by reference and available from the Agency for Health Care Administration, Division of Health Quality Assurance, Ft. Knox Office Building, 2727 Mahan Drive, Tallahassee, Florida 32308. The agency will make a determination of exemption status pursuant to the procedures in paragraph (5) of this rule and notify the hospital of the determination within 45 days of receipt of the request.

(c) Upon receipt of a hospital exemption request, the agency must act to approve or deny the exemption request within 45 days, during which time deemed exemption status does not exist. If the agency fails to notify the hospital of the status of the exemption request within the 45 day time frame, the hospital is deemed to be exempt from offering the service until such time that the agency acts to deny the request.

(d) When a hospital has been providing 24 hour per day, 7 day per week coverage either directly or indirectly through an agreement with another hospital or physician(s) for a specialty service as evidenced by the inventory and hospital license, and the circumstances significantly change such that the hospital can no longer provide the service on a 24 hour per day, 7 day per week basis, the hospital must apply for an exemption from the agency. The agency will make a determination of exemption status pursuant to paragraph (5) of this rule and notify the hospital of the determination within 45 days of receipt of the request.

(e) When a hospital has been granted an exemption from providing a specialty service 24 hours per day, 7 days per week, either directly or indirectly through an agreement with another hospital or physician(s), and the agency has information to indicate that the circumstances forwarded by the hospital, and accepted by the agency, as the basis for the granting of the exemption have changed, the agency will notify the hospital of this information and shall provide the hospital with an opportunity to respond. If the change in circumstances is confirmed and the hospital failed to report the change, the agency will amend the inventory accordingly and add the service capability to the face of the hospital license accordingly. Revocation of exemption status shall be effective upon the expiration of 21 days following the hospital's receipt of the agency decision or the entry of a final order if appealed.

(f) Each hospital shall immediately report any change in the conditions which led to the granting of an exemption.

(5) AGENCY REVIEW PROCESS. The review process for exemption requests shall be as follows:

(a) Upon receipt of application, the agency shall schedule an on-site visit at the hospital when deemed necessary to verify the facts as set forth in the application. The hospital will be notified of the date of the visit in advance. The agency shall have access to all records necessary for the confirmation and substantiation of the information submitted in the application and to any other records deemed necessary by the agency to make a determination.

(b) Upon receipt of an application, the agency shall publish, in the next available Florida Administrative Weekly, notice of receipt of the application, identifying the applicant and the service(s) for which exemption is requested. Comments submitted within 15 days of the date of publication will be considered by the agency prior to making a determination of exemption status.

(c) Within 45 days of receipt of application, the agency shall determine if the hospital has demonstrated that it meets the requirements for service exemption set forth in Section 395.1041, F.S. The agency shall notify the applicant in writing of its decision, and shall provide the applicant with specific reasons in the event that the request is denied.

(d) If the agency fails to notify the hospital of the status of the exemption request within the required 45 day time frame, pursuant to Section 395.1041(3)(d)4., F.S., the hospital is deemed to be exempt from offering the service until such time that the agency acts to deny the request.

(6) SERVICE DELIVERY REQUIREMENTS.

(a) Every hospital offering emergency services and care shall provide emergency care available 24 hours a day within the hospital to patients presenting to the hospital. At a minimum:

1. Emergency services personnel shall be available to ensure that emergency services and care are provided in accordance with Section 395.002(10), F.S.

2. At least one physician shall be available within 30 minutes through a medical staff call roster; initial consultation through two-way voice communication is acceptable for physician presence.

3. Specialty consultation shall be available by request of the attending physician or by transfer to a designated hospital where definitive care can be provided.

(b) When a patient is transferred from one hospital to another, all pertinent medical information shall accompany the patient being transferred.

(c) Every hospital offering emergency services and care shall maintain a transfer manual, which shall include in addition to the requirements in paragraph (2) of this rule:

1. Decision protocols for when to transfer a patient;

2. A list of receiving hospitals with special care capabilities, including the telephone number of a contact person;

3. A list of all “on-call” critical care physicians available to the hospital, including their telephone numbers; and

4. Protocols for receiving a call from a transferring hospital, including:

a. Requirements for specific information regarding the patient’s problem;

b. Estimated time of patient arrival;

c. Specific medical requirements;

d. A request to transfer the patient’s medical record with the patient; and

e. The name of the transporting service.

(d) Both transferring and receiving hospitals shall assign a specific person on each shift who shall have responsibility for being knowledgeable of the transfer manual and maintaining it.

(e) Each hospital offering emergency services and care shall maintain written policies and procedures specifying the scope and conduct of emergency services to be rendered to patients. Such policies and procedures must be approved by the organized medical staff, reviewed at least annually, revised as necessary, dated to indicate the time of last review, and enforced. Such policies shall include requirements for the following:

1. Direction of the emergency department by a designated physician who is a member of the organized medical staff.

2. A defined method of providing for a physician on call at all times.

3. Supervision of the care provided by all nursing service personnel with the emergency department by a designated registered nurse who is qualified by relevant training and experience in emergency care.

4. A written description of the duties and responsibilities of all other health personnel providing care within the emergency department.

5. A planned formal training program on emergency access laws, and participation, by all health personnel working in the emergency department.

6. A control register adequately identifying all persons seeking emergency care be established, and that a medical record be maintained on every patient seeking emergency care that is incorporated into the patient’s permanent medical record and that a copy of Florida EMS Report, HRS 1894, as required by Rule 64E-2.013, F.A.C., be included in the medical record, if the patient was delivered by ambulance. The control register must be continuously maintained and shall include at least the following for every individual seeking care:

a. Identification to include patient name, age and sex;

b. Date, time and means of arrival;

c. Nature of complaint;

d. Disposition; and

e. Time of departure.

(f) Every hospital offering emergency services and care shall have a method for assuring that a review of emergency patient care is performed and documented at least monthly, using the medical record and preestablished criteria.

(g) Every hospital offering emergency services and care shall insure the following:

1. That clinical laboratory services with the capability of performing all routine studies and standard analyses of blood, urine, and other body fluids are readily available at all times to the emergency department.

2. That an adequate supply of blood is available at all times, either in-hospital or from an outside source approved by the organized medical staff, and that blood typing and cross-matching capability and blood storage facilities are readily available to the emergency department.

3. That diagnostic radiology services within the service capability of the hospital are readily available at all times to the emergency department.

4. That the following are available for immediate use to the emergency department at all times:

a. Oxygen and means of administration;

b. Mechanical ventilatory assistance equipment, including airways, manual breathing bag, and ventilator;

c. Cardiac defibrillator with synchronization capability;

d. Respiratory and cardiac monitoring equipment;

e. Thoracentises and closed thoracostomy sets;

f. Tracheostomy or cricothyrotomy set;

g. Tourniquets;

h. Vascular cutdown sets;

i. Laryngoscopes and endotracheal tubes;

j. Urinary catheters with closed volume urinary systems;

k. Pleural and pericardial drainage set;

l. Minor surgical instruments;

m. Splinting devices;

n. Emergency obstetrical pack;

o. Standard drugs as determined by the facility, common poison antidotes, syringes and needles, parenteral fluids and infusion sets, and surgical supplies;

p. Refrigerated storage for biologicals and other supplies requiring refrigeration, within the emergency department; and

q. Stable examination tables.

(7) Each hospital offering emergency services and care shall have the capability to communicate via two-way radio with licensed EMS providers and their primary communications centers. The two-way radio communications system must meet the following provisions:

(a) Conform to the State EMS Communications Plan applicable to emergency room or department communications; and

(b) Any new communications system or an expansion of an existing communication system shall be approved by the Department of Management Services, Division of Communications, prior to purchasing.

Rulemaking Authority 395.1031, 395.1041, 395.1055 FS. Law Implemented 395.1031, 395.1041, 395.1055 FS. History–New 9-4-95, Formerly 59A-3.207.

## 59A-3.270 Health Information Management.

(1) Each hospital shall establish processes to obtain, manage, and utilize information to enhance and improve individual and organizational performance in patient care, governance, management, and support processes. Such processes shall:

(a) Be planned and designed to meet the hospital’s internal and external information needs;

(b) Provide for confidentiality, security and integrity;

(c) Provide uniform data definitions and methods for capturing and storing data, including electronic mediums and optical imaging;

(d) Provide education and training in information management principles to decision-makers and other hospital personnel who generate, collect, and analyze information;

(e) Transmit information in a timely and accurate manner; and

(f) Provide for the manipulation, communication and linkage of information.

(2) All hospitals involved in the transplantation of organs or tissues shall maintain a centralized tracking system to record the receipt and disposition of all organs and tissues transplanted within the hospital.

(a) The tracking system must be kept separate from patients’ medical records, and shall include at a minimum:

1. The organ or tissue type;

2. The donor identification number;

3. The name and license number of the procurement or distribution center supplying the organ or tissue;

4. Recipient information, including, at a minimum the patient’s name and identification number;

5. The name of the physician who performed the transplant;

6. The date the organ or tissue was received by the hospital; and

7. The date the organ or tissue was transplanted.

(b) This information must be provided, on a quarterly basis, to the organ procurement organization or tissue bank that originally provided the organ or tissue.

(3) Each hospital shall maintain a current and complete medical record for every patient seeking care or service. The medical record shall contain information required for completion of birth, death and still birth certificates, and shall, at a minimum contain the following information:

(a) Identification data;

(b) Chief complaint or reason for seeking care;

(c) Present illness;

(d) Personal medical history;

(e) Family medical history;

(f) Physical examination report;

(g) Provisional and pre-operative diagnosis;

(h) Clinical laboratory reports;

(i) Radiology, diagnostic imaging, and ancillary testing reports;

(j) Consultation reports;

(k) Medical and surgical treatment notes and reports;

(l) Evidence of appropriate informed consent;

(m) Evidence of medication and dosage administered;

(n) A copy of Florida EMS Report, HRS Form 1894, given to the hospital as required by Rule 64E-2.013, F.A.C., if the patient was delivered to the hospital by ambulance;

(o) Tissue reports;

(p) Physician and nurse progress notes;

(q) Principal diagnosis, secondary diagnoses and procedures when applicable;

(r) Discharge summary;

(s) Appropriate social work services reports, if provided;

(t) Autopsy findings when performed;

(u) Individualized treatment plan;

(v) Clinical assessment of the patients needs;

(w) Certifications of transfer of the patient between hospitals as specified by Rule 59A-3.255, F.A.C.; and

(x) Routine Inquiry Form regarding request for organ donation in the event of the death of the patient.

(4) For patients undergoing operative or other invasive procedures the medical record policies shall also require:

(a) The recording of preoperative diagnoses prior to surgery;

(b) That operative reports be recorded in the health record immediately following surgery or that an operative progress note is entered in the patient record to provide pertinent information; and

(c) Postoperative information shall include vital signs, level of consciousness, medications, blood components, complications and management of those events, identification of direct providers of care, discharge information from the post-anesthesia care area.

(5) Medical records for ambulatory care patients shall consist of the information specified in subsections 59A-3.2085(7)(i), F.A.C.

(6) Each hospital shall have a patient information system, medical records department or similarly titled unit with administrative responsibility for medical records. The medical records department shall:

(a) Maintain a system of identification and filing to ensure the prompt location of a patient’s medical record. Patient records may be stored on electronic medium such as optical imaging, computer, or microfilm;

(b) Centralize all appropriate clinical information relating to a patient’s hospital stay in the patient’s medical record;

(c) Index, and maintain on a current basis, all medical records according to disease, operation and physician.

(7) Patient records shall have a privileged and confidential status and shall not be disclosed without the consent of the person to whom they pertain pursuant to Section 395.3025(4), F.S., but appropriate disclosure may be made without such consent to:

(a) Hospital personnel for use in connection with the treatment of the patient;

(b) Hospital personnel only for internal hospital administrative purposes associated with the treatment, including risk management and quality assurance functions;

(c) The Agency for Health Care Administration; or

(d) In any civil or criminal action, unless otherwise prohibited by law, upon the issuance of a subpoena from a court of competent jurisdiction and proper notice by the party seeking such records to the patient or his legal representative.

(8) The Department of Health and Rehabilitative Services may examine patient records of a licensed facility for the purpose of epidemiological investigations, provided that the unauthorized release of information by agents of the department which would identify an individual patient constitutes a misdemeanor of the second degree, punishable as provided in Sections 775.082 or 775.083, F.S.

(9) Any licensed facility shall, upon request, and only after discharge of the patient, furnish to any patient admitted or treated in the facility, or to any patient’s guardian, curator, or personal representative, or to anyone designated by the patient in writing, a true and correct copy of all of the patient’s records, including X-rays, which are in the possession of the licensed facility, provided the person requesting such records agrees to pay a reasonable charge for copying the records, pursuant to Section 395.3025, F.S. The per page fee is applicable to each page generated during copying of the medical record by the facility or from a copy service providing these services on behalf of the facility. Progress notes and consultation reports of a psychiatric or substance abuse nature concerning the care and treatment performed by the licensed facility are exempted from this requirement. The licensed facility shall further allow any such person to examine the original records in its possession, or microfilms or other suitable reproductions of the records stored on electronic mediums, upon such reasonable terms imposed to assure that the records will not be damaged, destroyed, or altered.

(a) The provisions of this section do not apply to any licensed facility whose primary function is to provide psychiatric care or substance abuse treatment to its patients.

(b) Disclosure of the medical records of inmates of any institution, facility or program of the Department of Corrections shall be made in conformance with Chapter 945, F.S., and applicable rules adopted thereunder.

(10) Each hospital operated by the Department of Children and Families and the Department of Corrections shall use a problem oriented medical record for each patient, which shall be initiated at the time of intake or admission and which shall contain all pertinent information required by this section.

(11) Each problem oriented medical record maintained by hospitals operated by the Department of Children and Families and the Department of Corrections shall be standardized within each hospital and shall be capable of providing easy comparison of basic information on medical records at all such hospitals. Each problem oriented medical record maintained by these hospitals shall contain at least the following information:

(a) A patient data base which compiles all known facts about the patient which have relevance to his health care, and which in addition to the other requirements of this section contains:

1. Comments and complaints as spoken by the patient or other persons significant in the patient’s life, including relatives, friends and caretakers;

2. A patient profile, including health related habits, social, nutritional and educational information, and a review of physical systems;

3. Relevant legal documents, including but not limited to status forms, forensic forms, consent forms, authority permits, and Baker Act forms; and

4. A medical diagnosis listed according to the International Classification of Diseases and a mental illness diagnosis listed according to the Diagnosis and Statistical Manual of Mental Disorders, as relevant to the patient’s condition.

(b) A problem list, which is a table of contents to the patient’s record, which identifies by number, date and description of the patients problems.

(c) A plan of care which shall specify the specific course of action to be taken to address the problem(s) described, including diagnosis, diagnostic and therapeutic orders, treatment, examination, patient education, referral, and other necessary activities.

(d) Progress notes which shall document the activity and follow-up undertaken for each problem in a structured format which is dated, titled and numbered according to the problem to which it relates.

(12) The discharge summary of each problem oriented medical record in hospitals operated by the Department of Children and Families and the Department of Corrections shall be completed, signed and dated within 15 days following the patient’s discharge. The summary shall include:

(a) The reason for admission;

(b) A recapitulation of the patient’s hospitalization;

(c) A statement of the patient’s progress and condition upon discharge;

(d) The facility or person, including the patient himself when relevant, assuming responsibility for the patient after discharge; and

(e) Recommendations, when necessary, for after care, follow-up, referral or other action necessary to help the patient deal with problems.

Rulemaking Authority 395.1055, 395.3015 FS. Law Implemented 395.1055, 395.3015, 395.3025 FS. History–New 9-4-95, Formerly 59A-3.214.

## 59A-3.271 Quality Improvement.

(1) General Provisions. Each hospital shall have a planned, systematic, hospital wide approach to the assessment, and improvement of its performance to enhance and improve the quality of health care provided to the public.

(a) Such a system shall be based on the mission and plans of the organization, the needs and expectations of the patients and staff, up-to-date sources of information, and the performance of the processes and their outcomes.

(b) Each system for quality improvement, which shall include utilization review, must be defined in writing, approved by the governing board, and enforced, and shall include:

1. A written delineation of responsibilities for key staff;

2. A policy for all privileged staff, whereby staff members do not initially review their own cases for quality improvement program purposes;

3. A confidentiality policy;

4. Written, measurable criteria and norms;

5. A description of the methods used for identifying problems;

6. A description of the methods used for assessing problems, determining priorities for investigation, and resolving problems;

7. A description of the methods for monitoring activities to assure that desired results are achieved and sustained; and

8. Documentation of the activities and results of the program.

(2) Each hospital shall have in place a systematic process to collect data on process outcomes, priority issues chosen for improvement, and the satisfaction of the patients. Processes measured shall include:

(a) Appropriate surgical and other invasive procedures;

(b) Preparation of the patient for the procedure;

(c) Performance of the procedure and monitoring of the patient;

(d) Provision of post-procedure care;

(e) Use of medications including prescription, preparation and dispensing, administration, and monitoring of effects;

(f) Results of autopsies;

(g) Risk management activities;

(h) Quality improvement activities including at least clinical laboratory services, diagnostic imaging services, dietetic services, nuclear medicine services, and radiation oncology services.

(3) Each hospital shall have a process to assess data collected to determine:

(a) The level and performance of existing activities and procedures,

(b) Priorities for improvement, and

(c) Actions to improve performance.

(4) Each hospital shall have a process to incorporate quality improvement activities in existing hospital processes and procedures.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055 FS. History–New 9-4-95, Formerly 59A-3.216.

## 59A-3.272 Governing Body.

(1) The licensee shall have a governing body responsible for the conduct of the hospital as a functioning institution.

(2) The governing body shall be organized under written bylaws, rules and regulations which it reviews at least every two years, dates to indicate time of last review, revises as necessary, and enforces. Governing body by-laws shall:

(a) State the role and purpose of the hospital, including an organizational chart defining the lines of authority. The description of the structure of the hospital shall include full disclosure in writing of the names and addresses of all owners and persons controlling 5 percent or more interest in the hospital. In the case of corporations, holding companies, partnerships, and similar organizations, the names and addresses of officers, directors, and stockholders, both beneficial and of record, when holding 5 percent or more interest, shall be disclosed.

(b) State the qualifications for governing body membership, and the method of selecting members as well as the terms of appointment or election of members, officers and chairmen of committees.

(c) Provide for the designation of officers, their duties, and for the organization of the governing body into essential committees with the number and type consistent with the size and scope of the hospital's activities.

(d) Coordinate through an executive committee or the governing body as a whole, the policies and activities of the facility and special committees established by the governing body.

(e) Specify the frequency of meetings, at regularly stated intervals, the number or percentage of members constituting a quorum, and require that minutes be recorded and made available to all members of the governing body.

(3) The governing body shall establish the position of chief executive officer or other similarly titled position, and define in writing the responsibility, authority and accountability of the chief executive officer for operation and maintenance of the hospital.

(4) The governing body shall approve the by-laws, rules and regulations of the organized medical staff, provide for the appointment, reappointment, or dismissal of members of the organized medical staff, and provide a procedure for hearings and appeals on all actions concerning appointment, reappointment or dismissal. No action on appointment, reappointment, or dismissal of a member of the organized medical staff shall be taken without prior referral to the organized medical staff for their recommendation, except in emergency cases.

(a) The governing body shall provide that no qualified applicant is denied organized medical staff privileges or clinical privileges solely because the applicant is licensed as a physician, dentist or podiatrist.

(b) The governing body shall set standards and procedures to be applied by the hospital and the organized medical staff in considering and acting upon applications for staff membership or professional privileges, including delineation of privileges. Such standards or procedures shall be available for public inspection, and shall not operate to deny staff privileges or clinical privileges in an arbitrary, unreasonable or capricious manner, or on the basis of sex, race, creed, or national origin.

(c) When the standards and procedures established by the governing body require, as a precondition to obtaining staff membership or professional clinical privileges, the completion of or eligibility in, a program established by the American Medical Association or the Liaison Committee on Graduate Medical Education, the governing body shall also make available staff membership or privileges to physicians who have obtained the completion of or eligibility in, any program which is in the same area of medical specialization established by the American Osteopathic Association.

(d) The governing body shall require a delineation of privileges for each member of the organized medical staff. The delineation of privileges shall not be stated simply as a specialty designation, such as “general surgery” or “general medicine” unless such terms are specifically defined elsewhere.

(e) The governing body shall require that eligibility for privileges, delineation of privileges, and reappointments, be based on the applicant’s background, experience, health, training, demonstrated current competence, adherence to applicable professional ethics, reputation, ability to work with others, ability of the hospital to provide adequate facilities and supportive services for the applicant and his patients, and such other elements as the governing body determines that are not inconsistent with this part.

(f) The governing body shall establish a procedure, within a time-limited period, for approving, approving in part, or denying an applicant’s request for privileges.

(g) The governing body shall establish a procedure for an applicant for privileges to appeal an adverse decision, and shall establish a time-limited period for rendering a final decision after the appeal.

(h) The governing body shall set standards and procedures which provide for reasonable access by licensed chiropractors to the reports of diagnostic x-rays and laboratory tests of the institutions licensed facilities, subject to the same standards and procedures as other licensed physicians. However, nothing contained in the provisions of this section shall require a licensed facility to grant staff privileges to a chiropractor.

(5) The governing body of any licensed facility, is authorized to suspend, deny, revoke, or curtail the staff privileges of any staff member for good cause.

(a) The procedures for such actions shall comply with the facility’s established bylaws, standards, and procedures.

(b) The proceedings and records of committees and governing bodies which relate solely to actions taken in carrying out the provisions of this section shall not under any circumstances be subject to inspection under the provisions of Chapter 119, F.S.; nor shall meetings held pursuant to achieving the objectives of such committees and governing bodies be open to the public under the provisions of Chapter 286, F.S.

(c) Good cause shall include, but not be limited to:

1. Incompetence.

2. Negligence.

3. Being found to be a habitual user of intoxicants or drugs to the extent that he is deemed dangerous to himself or others.

4. Mental or physical impairment which may adversely affect patient care.

5. Behavior disruptive to the hospital environment.

(6) Within 30 days of receipt of a written request, either by an applicant for staff privileges, or by a member of the organized medical staff whose privileges have been suspended, denied, revoked or curtailed, whether in whole or in part, the licensed facility shall supply the reasons for such action in writing to the requesting applicant or staff member. A denial of staff membership or professional clinical privileges to any applicant shall be submitted, in writing, to the applicant’s respective licensing board.

(7) Nothing herein shall prohibit the licensee of the facility from acting as the governing body, provided that the articles of incorporation or other written organizational plan describe the manner in which the licensee executes the governing body’s responsibility.

Rulemaking Authority 395.1055 FS. Law Implemented 395.0191, 395.0193, 395.0195, 395.1055 FS. History–New 9-4-95, Formerly 59A-3.217.

## 59A-3.273 Management and Administration.

(1) Each hospital shall be under the direction of a chief executive officer appointed by the governing body, who is responsible for the operation of the hospital in a manner commensurate with the authority conferred by the governing body.

(2) The chief executive officer shall take all reasonable steps to provide for:

(a) Compliance with applicable laws and regulations; and

(b) The review of and prompt action on reports and recommendations of authorized planning, regulatory, and inspecting agencies.

(3) The chief executive officer shall provide for the following:

(a) Establishment and implementation of organized management and administrative functions, including:

1. Clear lines of responsibility and accountability within and between department heads and administrative staff;

2. Effective communication mechanisms among departments, medical staff, the administration and the governing body;

3. Internal controls;

4. Coordination of services with the identified needs of the patient population;

5. A policy on patient rights and responsibilities;

6. A mechanism for receiving and responding to complaints concerning patient care;

7. A policy on withholding resuscitative services;

8. Policies and procedures on identification and referral of organ and tissue donors including notification of organ and tissue procurement agencies when organs and tissues become available as specified under Rule 59A-3.219, F.A.C.;

9. Policies and procedures for meeting the communication needs of multicultural populations and persons with impaired hearing or speaking skills;

10. Policies and procedures on discharge planning;

11. A policy to assist in accessing educational services for children or adolescents when treatment requires a significant absence from school;

12. Policies and procedures to assure that the treatment, education and developmental needs of neonates, children and adolescents transferred from one setting to another are assessed;

13. Dissemination and enforcement of a policy prohibiting the use of smoking materials in hospital buildings and procedures for exceptions authorized for patients by a physician’s written authorization;

14. A policy regarding the use of restraints and seclusion; and

15. A comprehensive emergency management plan which meets the requirements of paragraph 395.1055(1)(c), F.S., and Rule 59A-3.078, F.A.C.

(b) Personnel policies and practices which address:

1. Non-discriminatory employment practices;

2. Verification of credentials including current licensure and certification;

3. Periodic performance evaluations; and

4. Provision of employee health services.

(c) Financial policies and procedures;

(d) An internal risk management program which meets the requirements of Section 395.0197, F.S., and Chapter 59A-10, F.S.C., and

(e) Assurance of compliance with educational requirements on human immunodeficiency virus and acquired immune deficiency syndrome pursuant to Sections 381.0034 and 381.0035, F.S., and Chapter 64D-2, F.A.C., September 1994.

Rulemaking Authority 395.1055 FS. Law Implemented 395.0197, 395.1055 FS. History–New 9-4-95, Formerly 59A-3.218.

## 59A-3.274 Anatomical Gifts, Routine Inquiry.

(1) Each Class I and Class II hospital shall establish a mechanism whereby the next of kin of all patients who are deemed medically acceptable and who die in Florida hospitals are given the opportunity to consider the donation of organs, tissues and eyes for transplantation and research.

(2) Education and Training of Designee. The hospital administrator or designee making the request of the next of kin for organ, tissue and eye donations shall be trained in the request procedures used in organ and tissue donation. The Organ Procurement Organization (OPO), tissue bank and eye bank shall, in conjunction with their affiliated hospitals, develop a requester training curriculum that will meet the individual needs of each affiliated hospital. The AHCA shall assist, if requested, in the implementation of the requester training curriculum in conjunction with an OPO, tissue bank and eye bank where the OPO, tissue bank and eye bank do not have adequate resources for the implementation of the requester training curriculum within their affiliated hospitals. This training shall include the following minimum basic curriculum:

(a) The criteria used by the affiliated OPO, tissue bank, and eye bank for determining the acceptability of patients as organ, tissue, or eye donors;

(b) The requirements of Florida law to be met in order for a donation to be allowed to proceed including:

1. Explanatory information regarding the family’s rights to allow or refuse a donation, to donate specific organs, tissues or eyes and to designate the organs, tissues or eyes for the purpose of transplantation, medical research or instruction, and

2. The criteria for determining whether a particular death falls within the scope of Section 406.11, F.S., necessitating close communication with the Medical Examiner’s office, and permission from the Medical Examiner when required;

(c) Necessary basic information regarding the process and procedures related to organ, tissue, and eye donation and transplantation including the following:

1. The procedures and techniques used in the recovery and preservation of organs, tissues and eyes;

2. The success rates of currently accepted transplant procedures;

3. The numbers of patients presently awaiting these procedures; and

4. The financial procedures and arrangements applicable to the donation of organs, tissues and eyes.

(d) The various approaches which can be used in dealing with a family in a grief situation and offering them the opportunity of organ, tissue, or eye donation. These approaches shall be based on the criteria of the affiliated OPO, tissue bank, and eye bank, which shall not be inconsistent with these guidelines;

(e) Notification of the affiliated OPO, tissue bank and eye bank; and

(f) Training regarding the administrative rules and guidelines promulgated by the agency for the purpose of implementing the Routine Inquiry provisions of the Anatomical Gift Act.

(3) Each Class I and Class II hospital or its designee shall, using the criteria of the affiliated OPO, tissue bank, and eye bank, implement the following procedures:

(a) Establish and publish a formal written policy and procedure for the identification and referral of organ, tissue, and eye donors. This policy shall include the procedure to be followed for the determination of brain death.

(b) Identify and designate the personnel or organization which will make the request for organ, tissue, or eye donation. These personnel shall be trained as required in paragraph (2) above and shall be available on a 24-hour “on call” basis to make the initial evaluations of donor suitability, request, and referrals.

(c) The Hospital Administrator or designee shall ensure that the District Medical Examiner is contacted in all medical examiners’ cases regarding the wishes of the family as to organ, tissue, and eye donation and to determine whether or not the medical examiner has released such organs, tissues or eyes for transplantation, medical research or instruction. This contact shall be recorded on the Routine Inquiry Form and placed in the patient’s medical record. When completion of the Routine Inquiry Form is designated by the hospital administrator and accepted by the affiliated procurement agency, the contact shall be noted in the records of the affiliated procurement agency. This notation shall indicate that request for donation of organs, tissue or eyes was made.

(d) The hospital administrator or designee shall ensure that all identified potential organ, tissue, or eye donors meeting the criteria of brain death as defined in Section 382.009, F.S., or cardiorespiratory death as defined in subsection 59A-3.065(9), F.A.C., shall be referred to the affiliated OPO, tissue bank, or eye bank for evaluation and recovery of the organs, tissues, or eyes to be donated according to the medical standards of the affiliated OPO, tissue bank and eye bank. This referral shall be recorded on the Routine Inquiry Form and placed in the patient's medical record. When completion of the Routine Inquiry Form is designated by the hospital administrator and accepted by the affiliated procurement agency, the referral shall be noted in the records of the affiliated procurement agency.

(e) The hospital shall work with the affiliated OPO, tissue bank, and eye bank to evaluate the patient as a potential organ, tissue, or eye donor. The medical acceptability of such organs, tissues, and eyes shall be determined according to the medical standards of the affiliated procurement agency. The hospital administrator may designate personnel of the affiliated OPO, tissue bank, or eye bank who shall make the request for donation. Where non-hospital personnel are designated to make the request for organ, tissue or eye donation, the affiliated OPO, tissue bank, or eye bank shall be given the opportunity to approach the next of kin about donation and shall utilize the following procedure when approaching the next of kin:

1. The affiliated OPO shall be given the opportunity to approach the next of kin about donation of organs in all suitable vascular organ donor cases when the potential donor meets the medical standards of the affiliated OPO. Where the suitable vascular organ donor also meets the medical standards of the affiliated tissue bank or eye bank, and in the absence of a contrary agreement between the affiliated OPO, tissue bank, and eye bank, the affiliated OPO may represent the affiliated tissue bank and eye bank and approach the next of kin about donation in all suitable tissue and eye donor cases.

2. The affiliated tissue bank shall be given the opportunity to approach the next of kin about donation in all suitable tissue donor cases where the potential donor meets the medical standards of the affiliated tissue bank and where the affiliated OPO has not already approached the next of kin for donation of tissues and eyes in all non-suitable vascular organ donor cases. Where the suitable tissue donor also meets the medical standards of the affiliated eye bank, and in the absence of a contrary agreement between the affiliated tissue bank and eye bank, the affiliated tissue bank may represent the affiliated eye bank and approach the next of kin about donation in all suitable eye donor cases.

3. The affiliated eye bank shall be given the opportunity to approach the next of kin about donation in all suitable eye donor cases where the potential donor meets the medical standards of the affiliated eye bank, and where the affiliated OPO or tissue bank has not already approached the next of kin for donation of eyes. Where the suitable eye donor also meets the medical standards of the affiliated tissue bank, and in the absence of a contrary agreement between the affiliated eye bank and tissue bank, the affiliated eye bank may represent the affiliated tissue bank and approach the next of kin about donation in all suitable tissue donor cases.

(f) The request for organ, tissue, or eye donation shall be made at or near the time of death, and in a manner which is conducive to the discussion of organ, tissue, and eye donation with the grieving next of kin according to the priority specified in Section 765.512, F.S.

(g) A Routine Inquiry Form shall be completed upon every patient death occurring within the hospital and shall become a part of each patient’s medical record.

1. The form shall document whether the patient was deemed medically suitable for donation of organs, tissues and eyes, and if the patient is not medically suitable for donation, the form shall document the specific reason according to the criteria of the affiliated procurement agency.

2. If the patient is deemed medically acceptable for donation, the form shall document that the patient’s appropriate next of kin was approached, as well as the outcome of the patient’s expressed wishes, if known, regarding the donation of organs, tissues, and eyes. If the family allows donation, a specific consent form shall be signed or completed by means of telegraphic, recorded telephonic, or other recorded message by the appropriate next of kin as specified in Section 765.512, F.S.

3. If a request for donation is deemed to be exempted according to paragraph (4) of this section, or the medical standards of the affiliated OPO, tissue bank, and eye bank, the form shall document the specific reason for the lack of a request.

(h) The lack of request and a complete written explanation shall be noted on the Routine Inquiry Form and made a part of the patient’s medical record or if designated by the hospital administrator, and accepted by the affiliated procurement agency, in the affiliated procurement agency’s records. If the affiliated procurement agency has been designated, the patient’s medical record shall document the referral of the potential donor to the affiliated procurement agency. All Routine Inquiry Forms maintained by the affiliated procurement agency shall be complete and include the patient’s name and medical record number. These records shall be made available to the hospital during normal working hours. A copy of the form shall be sent to the AHCA for data analysis. The referral of the affiliated procurement agency shall be documented in the patient’s medical record. This documentation shall include the name of the procurement agency and time and date of the referral. This referral shall be documented in the patient’s death record.

(i) Each Class I and Class II hospital or designee shall, on a quarterly basis, aggregate the statistical data relating to organ, tissue, and eye donation requests as required by the agency and forward them to the agency on the Donation Request Summary Data Form, AHCA Form 3130-8006-February 94, which is incorporated by reference. The affiliated OPO, tissue bank and eye bank may agree to be designated by the hospital administrator to aggregate and forward the required AHCA forms to the agency. This form shall be submitted on a quarterly basis, due on April 15, July 15, October 15 and January 15, for the respective previous quarters. This information shall be made available by the agency upon written request from an OPO, tissue bank or eye bank.

(4) Request Exemptions.

(a) The appropriate next of kin as defined by Section 732.912, F.S., of patients deemed medically acceptable by the medical standards of the affiliated OPO, tissue bank and eye bank, and dying in the hospital shall be asked about organ, tissue, and eye donation except as follows:

1. There is on record notification of prior objection by the individual, or the appropriate next of kin as defined by Section 732.912, F.S., or

2. The appropriate next of kin is in a violent state, or cannot be found after a reasonable search; or

3. No positive identification of the potential donor has been found; or

4. The medical examiner has denied permission; or

5. The hospital or designee, in accordance with a request for the affiliated procurement agency, has agreed to delay the request until the family has left the hospital.

Rulemaking Authority 765.522, 873.01(3)(a) FS. Law Implemented 765.522, 873.01(3)(a) FS. History–New 9-4-95, Formerly 59A-3.219.

## 59A-3.275 Organized Medical Staff.

(1) Each hospital shall have an organized medical staff organized under written by-laws approved by the governing body and responsible to the governing body of the hospital for the quality of all health care provided to patients in the facility and for the ethical and professional practices of its members.

(2) Each hospital’s organized medical staff shall determine its appropriate committee structure and shall provide that the following required committee functions are carried out with sufficient periodicity to assure their objectives being achieved by separate committee, combined committees, or committee of the whole:

(a) Coordination of the activities and general policies of the various departments.

(b) Interim decision making for the organized medical staff between staff meetings, under such limitations as shall be set by the organized medical staff.

(c) Follow-up and appropriate disposition of all reports dealing with the various staff functions.

(d) Review of all applications for appointment and reappointment to all categories of staff, and recommendations on each to the governing body, including delineation of privileges to be granted in each case, and right of hearing and appearance. Except in emergency cases, recommendations to the governing body for withdrawal of any privileges of a member of the organized medical staff or dismissal from the organized medical staff will be made only after a thorough investigation by the organized medical staff or a committee thereof, with the subject member being given the right of hearing before the organized medical staff or a committee thereof, if requested within a reasonable time as specified in the hospital’s by-laws.

(e) Medical records currently maintained describing the condition, treatment, and progress of patient in sufficient completeness to assure transferable comprehension of the case at any time.

(f) Clinical evaluation of the quality of medical care provided to all categories of patients on the basis of documented evidence.

(g) Review of hospital admissions with respect to need for admission, length of stay, discharge practices and evaluation of the services ordered and provided.

(h) Surveillance of hospital infection potentials and cases and the promotion of a preventive and corrective program designed to minimize these hazards.

(i) Surveillance of pharmacy and therapeutic policies and practices within the institution.

(j) Hospital tests may be ordered only by the attending physician, or by another licensed health professional if that licensed health professional is acting within his scope of practice as defined by applicable laws and rules of the agency. Nothing herein shall be construed to expand or restrict such laws and rules pertaining to the practice of the various health professions.

Rulemaking Authority 395.1055 FS. Law Implemented 395.0191, 395.1055, 395.301 FS. History–New 9-4-95, Formerly 59A-3.220.

## 59A-3.276 Maintenance.

(1) Each hospital shall develop, implement, and maintain a written preventive maintenance plan, in conjunction with the policies and procedures developed by the infection control committee, to ensure that the facility is maintained in accordance with the following:

(a) The interior and exterior of buildings shall be in good repair, free of hazards, and painted as needed.

(b) All patient care equipment shall be maintained in a clean, properly calibrated, and safe operating condition;

(c) All plumbing fixtures shall be maintained in good repair to assure proper functioning, and provided with back flow prevention devices, when required, to prevent contamination from entering the water supply;

(d) All mechanical and electrical equipment shall be maintained in working order, and shall be accessible for cleaning and inspection;

(e) Loose, cracked, or peeling wallpaper or paint shall be promptly replaced or repaired to provide a satisfactory finish;

(f) All furniture and furnishings, including mattresses, pillows, and other bedding; window coverings; including curtains, blinds, shades, and screens; and cubicle curtains or privacy screens, shall be maintained in good repair; and

(g) The grounds and buildings shall be maintained in a safe and sanitary condition and kept free from refuse, litter, and vermin breeding or harborage areas.

(2) Each hospital shall employ or otherwise arrange for sufficient personnel to implement and maintain its preventive maintenance program.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055 FS. History–New 9-4-95, Formerly 59A-3.222.

## 59A-3.277 Functional Safety.

(1) Each hospital shall have a hospital safety committee to adopt, implement and monitor a comprehensive, hospital wide safety program. The committee's functions and responsibilities may be assumed by another hospital committee. The committee shall adopt written policies and procedures to enhance the safety of the hospital, its personnel and patients. Such policies shall include but not be limited to the following:

(a) A method of coordination of the safety policies of the various hospital units, departments and committees;

(b) An incident reporting system;

(c) A method of conveying safety-related information to all hospital employees; and

(d) Conduct of a hazardous surveillance program at specifically defined intervals.

(2) In addition to other requirements, each hospital shall provide a complete system for patient identification within the hospital, including a system for all emergency room cases, including DOA, and disasters.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055 FS. History–New 9-4-95, Formerly 59A-3.223.

## 59A-3.278 Rehabilitation, Psychiatric and Substance Abuse Programs.

(1) All rehabilitation, psychiatric, and substance abuse programs provided by hospitals shall provide to the patient:

(a) An evaluation upon referral;

(b) Establishment of goals;

(c) Development of a plan of treatment, including discharge planning, in coordination with the referring individual and rehabilitation staff, and after discussion with the patient and family;

(d) Regular and frequent assessment, performed on an interdisciplinary basis, of the patient’s condition and progress, and of the results of treatment;

(e) Maintenance of treatment and progress records; and

(f) At least a quarterly assessment of the quality and appropriateness of the care provided.

(2) When any rehabilitation activity, psychiatric or substance abuse treatment is provided from outside the hospital, the source shall be available whenever needed for patient care, meet all safety requirements, abide by all pertinent rules and regulations of the hospital and medical staff, and document the quality assurance measures to be implemented.

(3) The scope of services offered, and the relationship of the rehabilitation, psychiatric or substance abuse program to other hospital units, as well as all supervisory relationships within the program, shall be defined in writing. Responsibility for the performance of clinical services also shall be clearly defined. Delegation of authority within the program shall be specified in job descriptions and in organizational plans. Written policies and procedures to guide the operation of the rehabilitation program shall be developed and reviewed at least annually, revised as necessary, dated to indicate the time of last revision, and enforced.

(4) There shall be a current written plan of care for each patient receiving rehabilitative, psychiatric or substance abuse services. The plan shall state the diagnosis, and problem list when appropriate, pertinent to the rehabilitation or treatment process; precautions necessitated by the patient’s general medical condition or other factors; the short-term and long-term goals of the treatment program; and require monthly or more frequent review of the patient’s progress. The medical record and the written plan shall evidence a team approach, with participation of the professional and administrative staffs, the patient, and, as appropriate, the patient’s family. The medical record shall document the written instructions given to the patient and the family concerning appropriate care after discharge from the hospital.

(5) The rehabilitation, psychiatric or substance abuse program must have notes and log records that are separately identified from the other admission and discharge records in the hospital in which it is located, and are separately retrievable.

(6) The beds assigned to the program must be physically separate from and not commingled with beds not included in the unit. Rehabilitation, psychiatric or substance abuse programs and beds may be located on the same floor as other programs or beds.

(7) In addition to meeting the requirements of (1) through (6) of this section, rehabilitation programs provided by hospitals must place responsibility for the medical direction of the rehabilitation program on a physician member of the organized medical staff who, on the basis of training, experience and interest, is knowledgeable in the rehabilitation services offered. Unless otherwise permitted by law, rehabilitation services shall be initiated by a physician. The written request for services shall include reference to the diagnosis or problems for which treatment is planned.

(8) In addition to meeting the requirements of (1)-(6) of this section, psychiatric, or substance abuse rehabilitation programs provided by hospitals shall meet at least the following additional standards:

(a) The program, unit, service or similarly titled part shall treat only those patients whose primary reason for admission was a diagnosis contained in the third edition of the American Psychiatric Association Diagnostic and Statistical Manual.

(b) The program, unit, service or similarly titled part shall have medical direction by an appropriately qualified practitioner, including a physician who is certified by the American Board of Psychiatry and Neurology or is eligible for examination by the Board or similar specialty board recognized by the American Osteopathic Association, a clinical psychologist, or a licensed physician with postgraduate training and experience in the diagnosis and treatment of nervous and mental disorders.

(c) The program, unit, service or similarly titled part shall furnish, through qualified personnel, psychological services, social work services, psychiatric nursing, occupational therapy, and recreational therapy, as appropriate to the needs of the patient.

(d) The program, unit, service or similarly titled part shall have a charge nurse who is a registered professional nurse qualified in psychiatric or mental health nursing.

(9) In addition to the medical direction required in subsection (7), overall supervision and administration of the following specialty rehabilitation programs may be provided by staff with the following credentials:

(a) Physical Therapy – A qualified physical therapist who shall be a graduate of a physical therapy program approved by a nationally recognized accrediting body or have documented equivalent training or experience, shall meet any current requirements for licensure or registration, and shall be currently competent in the field.

(b) Occupational Therapy – A qualified occupational therapist who shall be a graduate of an occupational therapy program approved by a nationally recognized accrediting body; or shall currently hold certification by the American Occupational Therapy Association as an Occupational Therapist, Registered; or shall have documented equivalent training or experience; and shall meet all current requirements for licensure under Chapter 468, Part IV, F.S.

(c) Speech Pathology and Audiology – A qualified speech-language pathologist or audiologist who shall hold the Certificate of Clinical Competence or a Statement of Equivalence in either speech pathology or audiology issued by the American Speech-Language-Hearing Association, or have documented equivalent training or experience; and shall meet all current requirements for licensure under Chapter 468, Part II, F.S.

(d) Rehabilitation Nursing – A professionally qualified licensed registered nurse who shall have documented training in rehabilitation nursing and at least one year of rehabilitation nursing experience.

(e) Vocational or Educational Rehabilitation – A qualified individual who shall be a graduate of vocational rehabilitation program at the graduate level, or have documented equivalent training or experience.

(f) Comprehensive Medical Rehabilitation – A qualified physician who shall be a member of the organized professional staff and who is certified, or eligible for examination, either by the American Board of Physical Medicine and Rehabilitation or by a specialty related to rehabilitation.

(10) Nothing in this section shall be construed to prevent a hospital from providing rehabilitation, psychiatric or substance abuse programs to its patients. However, no hospital shall have rehabilitation, psychiatric, intensive residential treatment program, or substance abuse beds unless it has obtained a valid certificate of need as required by Section 408.031 through 408.045, F.S., and meets the requirements of this section.

Rulemaking Authority 395.003, 395.1055 FS. Law Implemented 395.003, 395.1055, 408.032, 408.036 FS. History–New 9-4-95, Formerly 59A-3.229.

## 59A-3.279 Itemized Patient Bill.

(1) Within seven days following discharge or release from a licensed hospital not operated by the state, or within seven days after the earliest date at which the loss or expense from the service may be determined, the licensed hospital providing the service shall, upon request, submit to the patient, or to his survivor or legal guardian as may be appropriate, an itemized statement detailing in language comprehensible to an ordinary layman the specific nature of charges or expenses incurred by the patient, which in the initial billing shall contain a statement of specific services received and expenses incurred for such items of service, enumerating in detail the constituent components of the services received within each department of the licensed facility and including unit-price data on rates charged by the licensed facility.

(2) Each such statement shall:

(a) Not include charges of hospital-based physicians if billed separately.

(b) Not include any generalized category of expenses such as “other” or “miscellaneous” or similar categories.

(c) List drugs by brand or generic name and not refer to drug code numbers when referring to drugs of any sort.

(d) Specifically identify therapy treatment as to the date, type, and length of treatment when therapy treatment is a part of the statement. Any person receiving a statement pursuant to this section shall be fully and accurately informed as to each charge and service provided by the institution preparing the statement.

(3) On each such itemized statement there shall appear the words “A FOR-PROFIT (or NOT-FOR-PROFIT or PUBLIC) HOSPITAL LICENSED BY THE STATE OF FLORIDA” or substantially similar words sufficient to identify clearly and plainly the ownership status of the licensed facility.

(4) Each hospital shall document a procedure for providing, on a random sample basis, delivery of itemized bills to physicians and other members of the organized medical staff. Such procedure shall provide for the delivery of no less than 10 bills per year.

(5) In any billing for services subsequent to the initial billing for such services, the patient, or his survivor or legal guardian, may elect, at his option, to receive a copy of the detailed statement of specific services received and expenses incurred for each such item of service as provided in subsection (1).

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055, 395.301 FS. History–New 9-4-95, Formerly 59A-3.232.

## 59A-3.280 Child Abuse and Neglect.

(1) Every hospital admitting or treating shall adopt and incorporate a policy that requires every staff member to report any case of actual or suspected child abuse or neglect pursuant to Chapter 39, F.S.

(a) Each report of actual or suspected child abuse or neglect shall be made immediately to the Department of Children and Family Services’ Florida Abuse Hotline, statewide toll free number 1(800) 962-2873 or to the local office of the Department of Children and Family Services responsible for investigating such reports.

(b) Any person required to report suspected child abuse or neglect, who has reasonable cause to suspect that a child died as a result of abuse or neglect, shall report his suspicion to the local medical examiner.

(2) Physician Liaison. Each hospital admitting or treating children shall designate, at the request of the Department of Children and Family Services, a staff physician to act as a liaison between the hospital, the child protective investigator and the child protection team.

(3) Child Abuse and Neglect Policy Reporting. Each hospital admitting or treating children shall formulate a child abuse and neglect policy and shall submit a copy of this policy to the Department of Children and Family Services, Office of Family Safety, 1317 Winewood Boulevard – Building 1, Tallahassee, Florida 32399-0700.

(4) Remedies. Failure to comply with these rules will result in a fine being imposed in accordance with the provisions of Section 395.1023, F.S.

Rulemaking Authority 395.1055 FS. Law Implemented 39.303, 395.002, 395.1023, 395.1055 FS. History–New 4-17-97, Formerly 59A-3.0465.

## 59A-3.281 Spontaneous Fetal Demise.

When a spontaneous fetal demise occurs after a gestation of less than 20 completed weeks, the health care facility identified in Section 383.33625(4), F.S., shall follow the provisions of that section and shall provide AHCA Form 3100-0006, January 2005, Notification of Disposition of Fetal Demise, to the mother for her completion. AHCA Form 3100-0006, January 2005 is incorporated in this rule by reference and available at http://ahca.myflorida.com/MCHQ/Health_Facility_Regulation/Hospital_ Outpatient/hospital.shtml, or from the Hospital and Outpatient Services Unit at 2727 Mahan Drive MS #31, Tallahassee, FL 32308. A copy of the signed and completed form shall by retained in the mother’s birth center file and shall be available for review by the Agency or Department of Health.

Rulemaking Authority 383.33625(6) FS. Law Implemented 383.33625, 395.1055(1)(b), 395.3025(4)(c) FS. History–New 4-27-06.

## 59A-3.300 Licensure Procedure.

Programs desiring licensure under this rule shall follow the procedure as described in Rule 59A-3.066, F.A.C., and shall comply with the provisions of Rules 59A-3.301 through 59A-3.312, F.A.C., which establishes the minimum standards for the voluntary licensure as a special hospital of Joint Commission on Accreditation of Healthcare Organizations (JCAHO) accredited Intensive Residential Treatment Programs for Children and Adolescents. These rules emphasize the programmatic requirements designed to meet the needs of the patient in a safe therapeutic environment and are intended to be used in licensing intensive residential treatment facilities for children and adolescents as specialty hospitals pursuant to Section 395.002(16), F.S. Unless otherwise specified, Rules 59A-3.301 through 59A-3.312, F.A.C., supersede the requirements of Rules 59A-3.300 through 59A-3.312, F.A.C., for the purpose of licensing intensive treatment facilities for children and adolescents as specialty hospitals.

Rulemaking Authority 395.003, 395.004, 395.0161, 395.1055 FS. Law Implemented 395.002, 395.003, 395.004, 395.0161, 395.0191, 395.1055 FS. History–New 2-15-82, Amended 8-14-86, Formerly 10D-28.101, Amended 9-4-95, 4-17-97, Formerly 59A-3.101.

## 59A-3.301 Goals, Policies and Procedures.

Each program shall have a written statement of its purpose and objectives, which will include but not be limited to a formal, long range plan adopted to guide and schedule steps leading to attainment of its projected objectives. This plan shall include an officially promulgated description of the services the program offers so that there is a frame of reference for judging the various aspects of the program. Proposed changes in treatment programs must be reported to and approved by the appropriate licensing agency. The plan shall also include but not be limited to the following:

(1) A description of the target population including but not limited to age, types of disorders, sex, and financial requirements;

(2) The initial screening process;

(3) The intake/admission process;

(4) Methods for involving family members or significant others (i.e., guardians, counselors, friends) in assessment, treatment, discharge, and follow-up care plans;

(5) An organizational chart with a description of each unit or department and its services, goals, policies and procedures, staffing patterns and its relationship to other services and departments and how these are to contribute to the priorities and goals of the program;

(6) Ways in which the program carries out any community education consultation programs; and

(7) Ways in which the program provides or makes referrals or arrangements for other medical, health care, dental, special assessment and therapeutic services. This shall be in the plan for:

(a) Clinical services;

(b) Emergency services and crisis intervention;

(c) Educational services for all residents; and

(d) Discharge and follow-up care and evaluation.

Rulemaking Authority 395.003, 395.1055 FS. Law Implemented 395.002, 395.003, 395.1055 FS. History–New 2-15-82, Formerly 10D-28.105, 59A-3.105.

## 59A-3.302 Personnel.

(1) Composition. The composition of the staff shall be determined by the needs of the patients being served and the goals of the facility, and shall have available a sufficient number of mental health professionals, health care workers, program staff and administrative personnel to meet these goals.

(a) The administrator of the facility shall have a master’s degree in administration or be of a professional discipline related to child and adolescent mental health and have at least three (3) years administrative experience. A person with a baccalaureate degree may also qualify for administrator with seven (7) years experience of child and adolescent mental health care with no less than three (3) years administrative experience. Persons occupying this position on or before the effective date of these rules may be allowed to continue in this position.

(b) The clinical director shall be at least board eligible in psychiatry with the American Board of Psychiatry with experience in child and adolescent mental health.

(c) If the clinical director is not full-time, then there shall be a full-time service coordinator who is a mental health professional with at least a master’s degree who is experienced in child and adolescent mental health and is responsible for the coordination of treatment aspects of the program.

(d) Mental health professionals shall include, but are not limited to, psychiatrists, psychologists, and social workers. These persons, if not on a full-time basis, must be on a continuing consulting basis. The authority and participation of such mental health professionals shall be such that they are able to assume responsibility for supervising and reviewing the needs of the patients and the services being provided. Such individuals shall participate in specific functions, e.g., assessment, treatment planning, treatment plan and individual case reviews, and program planning and policy and procedure development and review.

(e) Other professional and paraprofessional staff shall include, but not be limited to, physicians, registered nurses, educators and 24-hour a day mental assistants. Also included on a regular staff basis, or as consultants on a continuing basis, shall be activity staff and vocational counselors; and

(f) Consultation shall be available as needed from dieticians, speech, hearing and language specialists, or other specialists.

(2) Organization. The program shall have an organizational plan which clearly explains the responsibilities of the staff. This plan shall also include:

(a) Lines of authority, accountability and communication;

(b) Committee structure and reporting or dissemination of material; and

(c) Established requirements regarding the frequency of attendance at general and departmental/service or team/unit meetings.

(3) Policies and Records. Personnel policies and practices shall be designed, established and maintained to promote the objectives of the program and to insure that there are personnel to support a high quality of patient care.

(a) Each program shall have a written personnel practice plan covering the following areas: job classification; pay plan; personnel selection; probation or work-test period; tenure of office; dismissal; salary increases; procedure for health evaluations; holidays; leave policies; training programs; work evaluation procedures; additional employment benefits; and personnel records. Each new employee shall be given a copy of personnel practices when hired and documentation of receipt shall be maintained in the employee’s personnel file. A procedure shall be established for notifying employees of changes in established policies.

(b) There shall be clear job descriptions for all personnel. Each description shall contain the position title, immediate supervisor, responsibilities and authority. These shall also be used as a basis for periodic evaluations by the supervisor.

(c) Accurate and complete personnel records shall be maintained on each employee. Content shall be established to include but not be limited to the following:

1. Current background information, including the application, references and any accompanying documentation sufficient to justify the initial and continued employment of the individual and the position for which he was employed. Applicants for the positions requiring a licensed person shall be employed only after the facility has obtained verification of their licenses. Where accreditation is a requirement, this shall also be verified. Evidence of renewal of license as required by the licensing agent shall be maintained in the employee’s personnel record;

2. Current information relative to work performance evaluation;

3. Records of pre-employment health examinations and subsequent health services rendered to employees, as are necessary to ensure that all facility employees are physically and emotionally able to perform their duties;

4. Medical reports that verify the absence of active communicable disease in facility employees; and

5. Record of any continuing education or staff development programs completed.

(4) Staff Development. The program must provide opportunities and motivation for continuous staff training to enable each member to add to his knowledge and skills and thus improve the quality of services offered. This must be documented.

(a) Programs shall be facility-based with a designated person or committee who is responsible, on a continuing basis, for planning and insuring that Plans are implemented. The facility shall also make use of educational programs outside the facility such as workshops, and seminars; and

(b) There shall be appropriate orientation and training programs available for all new employees.

Rulemaking Authority 395.003, 395.1055 FS. Law Implemented 395.002, 395.003, 395.1055 FS. History–New 2-15-82, Formerly 10D-28.106, 59A-3.106.

## 59A-3.303 Facilities and Physical Plant Safety.

(1) General Requirements. The facility shall plan and provide an environment that is therapeutic to, and supportive of, all the patients in regard to their disturbances, their healthy development and their changing needs. The therapeutic environment shall take into consideration the architecture of the facility, indoor and outdoor activity areas, furnishings, equipment, decorations and all other factors that involve the interpersonal and physical environment.

(2) Facilities shall:

(a) Be designed to meet the needs of the age group of the patients and the objectives of the program;

(b) Provide adequate and appropriate space and equipment for all of the programs of the facility and the various functions within the facility;

(c) Provide sufficient space and equipment to ensure housekeeping and maintenance programs capable of keeping the building and equipment clean and in good repair; and

(d) Provide buildings and grounds of the special hospital that shall be maintained, repaired and cleaned so that they are not hazardous to the health and safety of the patients and staff.

1. Floors, walls, ceilings, windows, doors and all appurtenances of the structures shall be of sound construction, properly maintained, easily cleanable and shall be kept clean.

2. All areas of the facility other than closets or cabinets shall be well lighted. Dormitories, toilets and dayrooms shall have light sources capable of providing adequate illumination to permit observation, cleaning, maintenance and reading. Light fixtures shall be kept clean and maintained.

3. All housing facilities shall be kept free of offensive odors with adequate ventilation.

a. If natural ventilation is utilized, the opened window area for ventilation purposes shall be equal to one- tenth of the floor space in the residential area.

b. When mechanical ventilation or cooling systems are employed, the system shall be kept clean and properly maintained. Intake air ducts shall be designed and installed so that dust or filters can be readily removed. In residence areas and isolation rooms without natural ventilation, mechanical ventilation systems shall provide a minimum of 10 cubic feet of fresh or filtered recirculated air per minute for each patient occupying the area.

c. All toilet rooms shall be provided with direct openings to the outside or provided with mechanical ventilation to the outside.

d. Facilities which utilize permanent heating units shall maintain a minimum temperature of 65 degrees F at a point 20 inches above the floor in sleeping areas. Facilities, such as outdoor programs, which cannot provide permanent heating units, shall ensure that patients are provided with items which will provide adequate warmth during sleep. These shall include items such as portable catalytic heaters and sleeping bags, extra blankets and clothing designed to ensure comfortable sleep in cold weather.

(e) Provide both indoor and outdoor areas where patients can gather for appropriate activities. The grounds on which the facility is located shall provide adequate space to carry out the stated goals of the program; for outdoor activity areas that are appropriate for the ages and clinical needs of children; and provide an appropriate transitional area between the facility and the surrounding neighborhood which is consistent with the goals of the facility, and compatible with existing zoning ordinances.

(f) Provide sleeping areas that shall promote comfort and dignity and provide space and privacy for residents.

1. There shall be no more than eight patients in a sleeping room unless written justification on the basis of the program requirements has been submitted to and approved by the licensing agency.

2. Beddings, Clothing and Personal Items. Beds and beddings shall be kept in good repair and cleaned regularly. Used mattress and pillow covers shall be laundered before being issued. Sheets and personal clothing shall be washed at least weekly and blankets washed or dry cleaned at least quarterly. Sheets and blankets shall be stored in a clean, dry place between laundering and issue.

3. Each patient shall have his own bed consisting of a level bedstead and a clean mattress in good condition.

4. All mattresses shall have fire retardant mattress covers or protectors. Water repellent mattress covers shall be available if needed.

(g) Provide individual and separate accessible storage areas for each resident’s clothing and personal possessions.

(h) Provide laundry and/or dry cleaning facilities. Where laundry facilities are provided, they shall be adequate to ensure an ample quantity of clean clothing, bed linens and towels. Laundry facilities shall be of sound construction and shall be kept clean and in good repair. Laundry rooms shall be well lighted and properly ventilated. Clothes dryers and dry cleaning machines shall be vented to the exterior. Exposure to dry cleaning solvents shall not exceed threshold limit values set by the American Conference of Governmental Hygienists. If laundry facilities are not available, sheets and blankets shall be sent to commercial laundries.

(i) Provide privacy for personal hygiene.

1. All toilets shall have secured seats and be kept clean and in good working order, and all toilets shall be partitioned for privacy.

2. Bathrooms shall be cleaned thoroughly each day.

3. Bathrooms shall be conveniently located to the sleeping areas.

(j) Provide for the personal hygiene for all patients.

1. A written policy shall be maintained on file at the facility.

2. Toothbrushes, toothpaste, soap, and other items of personal hygiene shall be provided by the facility if not provided by the patients.

3. Shatterproof mirrors shall be furnished in each bathroom.

(k) Maintain food service facilities in accordance with the regulations described in Chapter 64E-11, F.A.C.

(3) The facility shall be constructed and maintained in a manner that protects the lives and insures the physical safety of patients, staff and visitors. The center will comply with all relevant federal, state and local building codes, fire, health, safety laws and ordinances and regulations as specified below. Current inspection reports shall be retained in the facility’s files for AHCA review.

(a) It is the responsibility of the program to arrange for the necessary inspections and to comply within the time frame with any resulting recommendations noted in the inspection reports.

(b) The grounds and all buildings on the grounds shall be maintained in a safe and sanitary condition, as required in Chapter 386, F.S. (Nuisances Injurious to Health).

(c) Water Supply. Water supplies shall be adequate to serve the demands of the facility and shall be constructed, operated and maintained in accordance with requirements of Chapter 64E-8, F.A.C.

1. Drinking water shall be accessible to all clients. When drinking fountains are available, the jet of the fountain shall issue from a nozzle of non-oxidizing impervious material set at an angle from the vertical. The nozzle and every other opening in the water pipe or conductor leading to the nozzle shall be above the edge of the bowl so that such nozzle or opening will not be flooded in case a drain from the bowl of the fountain becomes clogged. The end of the nozzle shall be protected by non-oxidizing guards to prevent persons using the fountain from coming into contact with the nozzle. Vertical or bubbler drinking fountains shall be replaced with approved type water fountains or be disconnected. When no approved drinking fountains are available, clients shall be provided with single service cups which shall be stored and dispensed in a manner to prevent contamination. Common drinking cups are prohibited.

2. Hot and cold running water under pressure and at safe temperatures (not to exceed 120 degrees F for washing and bathing to prevent scalding) shall be provided at regular washing and bathing areas.

(d) Sanitary System, Facilities and Fixtures.

1. All sewage and liquid waste shall be disposed of in accordance with Chapter 64E-6, F.A.C.

2. All plumbing shall comply with the requirements of Chapter 9B-51, F.A.C., or the plumbing code legally applicable to the area where the facility is located.

3. For facilities with nine or more patients, curbed areas with floor drains shall be available in convenient locations throughout the facility for the proper disposal of cleaning water and to facilitate cleaning.

(e) Garbage and Rubbish. All garbage, trash and rubbish from residential areas shall be collected daily and taken to storage facilities. Garbage shall be removed from storage facilities at least twice per week. Wet garbage shall be collected and stored in impervious, leak proof, fly tight containers pending disposal. All containers, storage areas and surrounding premises shall be kept clean and free of vermin. If public or contract garbage collection service is available, the facility shall subscribe to these services unless the volume makes on-site disposal feasible. If garbage and trash are disposed on premises, the method of disposal shall not create sanitary nuisance conditions and shall comply with provisions of Chapter 64E-12.010, F.A.C.

(f) Outdoor Areas. Outdoor areas shall be kept free of litter and trash and be well drained. If swimming pools are available in facilities with nine or more clients, such pools shall comply with requirements of Chapter 64E-9, F.A.C., and shall be supervised at all times when they are in use. Indoor and outdoor recreational areas shall be provided with safeguards designed for the needs of the residents.

(g) Insect and Rodent Control. Facilities shall be kept free of all insects and rodents. All outside openings shall be effectively sealed or screened to prevent entry of insects or rodents. All pesticides used to control insects or rodents shall be applied in accordance with instructions on the registered product label. Persons applying restricted use pesticides shall be certified by the Department. Facilities not having certified pest control operators shall utilize commercial licensed pest control companies.

(4) All facilities shall be required to meet the uniform fire safety standards for special hospitals as established by the State Fire Marshal pursuant to Section 633.05(8), F.S.

(a) All staff shall be instructed in the use of fire extinguishers.

(b) All fire extinguishers shall be inspected as regulated by local requirements and shall be serviced as required.

(c) All fire safety systems shall be kept in good operating condition.

(d) Fire safety systems shall be inspected regularly as regulated by local requirements, and records of such inspections shall be kept on file.

(5) The special hospital shall provide for safety inspections by a facility personnel committee.

(a) Personnel responsible for safety evaluation shall receive appropriate training.

(b) Safety inspections shall be done on a monthly basis, shall be made into a written report, and shall be maintained on file at the facility.

(c) Special safety measures shall be provided for areas of the facility that may present an unusual hazard to patients, staff or visitors. Poisonous or toxic compounds are to be stored apart from food and other areas that would constitute a hazard to the residents.

(6) Disaster Planning. Programs licensed under Rules 59A-3.300 through 59A-3.312 shall comply with Rule 59A-3.078, F.A.C., in regard to a comprehensive emergency management plan.

Rulemaking Authority 395.1055 FS. Law Implemented 395.1055 FS. History–New 2-15-82, Formerly 10D-28.108, Amended 9-4-95, Formerly 59A-3.108.

## 59A-3.312 Exceptions.

Rulemaking Authority 395.003, 395.0163, 395.1055 FS. Law Implemented 395.002, 395.1055 FS. History–New 2-15-82, Formerly 10D-28.111, 59A-3.111, Repealed 5-14-12.